## Summary
Plant | PVDAQ-1278 (building D)
DC / AC [kW] | 171.4 / 150.0
Location | 36.1952, -115.1582
Report time zone | Etc/GMT+8
Months | 2016-01 .. 2018-12
Budget P50 [kWh] | 873294.5657
Actual [kWh] | 755069.2651
Deviation [%] | -13.54%
Bridge method | sequential
Unexplained residual [kWh] | -67823.6879
YoY performance trend [%/yr] | -0.6409%
QC findings (warn/fail) | 5
Note | Working material. PR definitions follow public descriptions of IEC 61724-1 and NREL weather-corrected PR; not a certified implementation. Contract clauses are examples.

## Bridge
Month | Coverage | Budget P50 [kWh] | Actual [kWh] | Deviation [kWh] | Deviation [%] | Irradiance [kWh] | Temperature [kWh] | Degradation [kWh] | Soiling [kWh] | Snow [kWh] | Clipping [kWh] | Availability [kWh] | Curtailment [kWh] | Data gaps [kWh] | Unexplained [kWh] | Check [kWh] | POA actual [kWh/m2] | POA budget [kWh/m2] | PR | PR weather-corr. | PR budget | Availability time | Availability energy
2016-01 | 100% | 17179.1909 | 11034.025 | -6145.1659 | -35.77% | -2364.0213 | -107.4764 | -319.4115 | -186.1889 | 0 | 0 | 136.9359 | 0 | 0 | -3305.0037 | 0 | 104.9243 | 121.3242 | 61.37% | 57.23% | 82.63% | 99.82% | 99.92%
2016-02 | 100% | 19243.7948 | 17998.6 | -1245.1948 | -6.471% | 3713.9878 | -1001.2299 | -485.488 | 332.9323 | 0 | -1.8657 | 208.9526 | 0 | -18.3139 | -3994.1699 | 0 | 161.4847 | 135.2342 | 65.04% | 62.57% | 83.04% | 99.95% | 99.96%
2016-03 | 100% | 25113.6512 | 23020.9 | -2092.7512 | -8.333% | 261.4276 | -691.3296 | -555.8463 | 34.56 | 0 | -16.9345 | 240.8897 | 0 | -7.3914 | -1358.1267 | 0 | 186.1357 | 184.0676 | 72.17% | 70.97% | 79.62% | 99.98% | 99.99%
2016-04 | 100% | 30011.3725 | 25194.375 | -4816.9975 | -16.05% | -4497.9734 | 480.4681 | -595.6675 | 199.517 | -151.5629 | -70.078 | 251.3652 | 0 | 0 | -433.0658 | 0 | 195.5823 | 229.5549 | 75.17% | 73.72% | 76.29% | 99.93% | 99.98%
2016-05 | 100% | 33583.6188 | 30078.7 | -3504.9188 | -10.44% | -3243.8115 | 190.0032 | -712.28 | 614.8919 | -169.6265 | -76.2652 | 301.1872 | 0 | 0 | -409.0177 | 0 | 236.4586 | 261.4334 | 74.23% | 74.74% | 74.96% | 100% | 100%
2016-06 | 100% | 32634.6477 | 28989.2 | -3645.4477 | -11.17% | -2770.6745 | -1439.207 | -674.4834 | 572.0528 | 0 | 0 | 242.5711 | 0 | 0 | 424.2933 | 0 | 242.0426 | 264.1272 | 69.89% | 76.58% | 72.1% | 99.87% | 99.87%
2016-07 | 100% | 29147.3367 | 30167.825 | 1020.4883 | 3.501% | 926.1107 | -1127.7497 | -698.6024 | 582.2943 | 0 | 0 | 285.3242 | 0 | 0 | 1053.1111 | -1.1369e-13 | 247.8813 | 239.9824 | 71.02% | 78.21% | 70.88% | 100% | 100%
2016-08 | 100% | 28128.3147 | 26360.725 | -1767.5897 | -6.284% | -875.4977 | -542.6609 | -655.9192 | 537.09 | 0 | -3.9251 | 263.1741 | 0 | 0 | -489.8509 | 0 | 222.8482 | 229.6603 | 69.03% | 74.27% | 71.47% | 100% | 100%
2016-09 | 100% | 24593.3806 | 23684.175 | -909.2056 | -3.697% | 915.6314 | 116.2449 | -639.624 | 502.6609 | 0 | -5.5044 | 252.3801 | 0 | 0 | -2050.9946 | 0 | 203.1129 | 195.563 | 68.05% | 69.98% | 73.39% | 100% | 100%
2016-10 | 100% | 20389.403 | 18181.9 | -2207.503 | -10.83% | 446.2499 | 255.9385 | -534.7506 | 186.07 | 0 | -6.1697 | 193.6515 | 0 | 0 | -2748.4926 | 0 | 157.3907 | 153.7877 | 67.41% | 65.62% | 77.37% | 99.88% | 99.92%
2016-11 | 100% | 16928.0896 | 14309.2 | -2618.8896 | -15.47% | 1319.2879 | -317.5904 | -462.1269 | -109.5843 | 0 | 0 | 173.1068 | 0 | 0 | -3221.9827 | 0 | 131.2178 | 121.565 | 63.64% | 60.88% | 81.26% | 99.87% | 99.98%
2016-12 | 100% | 14146.9728 | 10393.675 | -3753.2978 | -26.53% | -389.5219 | 245.3897 | -366.5065 | -113.7478 | 0 | 0 | 137.7407 | 0 | -572.9125 | -2693.7394 | 0 | 95.8128 | 98.2822 | 63.3% | 56.82% | 84% | 100% | 100%
2017-01 | 100% | 17179.1909 | 11963.2 | -5215.9909 | -30.36% | -1983.6116 | -91.104 | -402.1718 | 119.6333 | 0 | 0 | 148.5081 | 0 | -780.4935 | -2226.7514 | 0 | 107.5905 | 121.3242 | 64.89% | 60.44% | 82.63% | 100% | 100%
2017-02 | 100% | 19243.7948 | 14023.275 | -5220.5198 | -27.13% | -3100.3446 | -174.1246 | -431.2664 | -744.9851 | 0 | 0 | 156.9501 | 0 | 0 | -926.7492 | 0 | 113.8668 | 135.2342 | 71.87% | 67.05% | 83.04% | 100% | 100%
2017-03 | 100% | 25113.6512 | 21768.725 | -3344.9262 | -13.32% | 1000.0334 | 156.0988 | -719.5596 | 526.7001 | -109.0104 | -60.0259 | 252.2563 | 0 | -1627.1212 | -2764.2978 | 0 | 191.5073 | 184.0676 | 66.33% | 63.28% | 79.62% | 99.92% | 99.97%
2017-04 | 100% | 30011.3725 | 27974.05 | -2037.3225 | -6.789% | -1180.1261 | 371.0145 | -811.9806 | 585.3482 | 0 | -111.0697 | 257.0637 | 0 | -25.1574 | -1122.4151 | 0 | 220.8136 | 229.5549 | 73.93% | 72.89% | 76.29% | 99.86% | 99.89%
2017-05 | 100% | 33583.6188 | 30680.675 | -2902.9438 | -8.644% | -2222.5216 | -417.371 | -872.7653 | 620.1181 | 0 | -25.6747 | 303.7471 | 0 | 0 | -288.4763 | 0 | 244.3484 | 261.4334 | 73.27% | 75.08% | 74.96% | 100% | 100%
2017-06 | 100% | 32634.6477 | 30254.575 | -2380.0727 | -7.293% | -1542.5922 | -1343.597 | -851.1364 | 595.6982 | 0 | -4.2238 | 283.7253 | 0 | 0 | 482.0532 | 0 | 251.897 | 264.1272 | 70.09% | 76.44% | 72.1% | 99.94% | 99.97%
2017-07 | 100% | 29147.3367 | 26417.525 | -2729.8117 | -9.366% | -2390.1404 | -925.1813 | -749.4508 | 488.2907 | 0 | 0 | 253.3592 | 0 | 0 | 593.3109 | 0 | 220.6577 | 239.9824 | 69.87% | 76.7% | 70.88% | 100% | 100%
2017-08 | 100% | 28128.3147 | 25958.45 | -2169.8647 | -7.714% | -1489.5222 | -597.5937 | -766.3751 | 469.8904 | 0 | 0 | 255.3012 | 0 | 0 | -41.5653 | 0 | 217.8694 | 229.6603 | 69.53% | 74.97% | 71.47% | 100% | 100%
2017-09 | 100% | 24593.3806 | 22712.825 | -1880.5556 | -7.647% | -754.0227 | 361.4065 | -722.2883 | 483.9925 | 0 | -11.4135 | 236.4235 | 0 | 0 | -1474.6536 | 0 | 189.8889 | 195.563 | 69.8% | 71.1% | 73.39% | 99.98% | 100%
2017-10 | 100% | 20389.403 | 13359.975 | -7029.428 | -34.48% | 3886.2515 | 85.0506 | -736.5102 | 394.9758 | 0 | -2.3852 | -5869.1507 | 0 | 0 | -4787.6597 | 0 | 183.1739 | 153.7877 | 42.56% | 41.76% | 77.37% | 66.01% | 68.63%
2017-11 | 100% | 16928.0896 | 3825.575 | -13102.5146 | -77.4% | 427.3471 | 206.1809 | -538.1471 | -27.5541 | 0 | 0 | -2941.9425 | 0 | -6840.2883 | -3388.1105 | 0 | 124.8672 | 121.565 | 17.88% | 16.66% | 81.26% | 56.3% | 55.13%
2017-12 | 100% | 14146.9728 | 11249.625 | -2897.3478 | -20.48% | 3038.1941 | 66.6862 | -535.6421 | -313.4275 | 0 | 0 | 168.8506 | 0 | -1259.6571 | -4062.352 | 0 | 119.3403 | 98.2822 | 55.01% | 49.99% | 84% | 100% | 100%
2018-01 | 100% | 17179.1909 | 12975.25 | -4203.9409 | -24.47% | -285.2899 | -559.3496 | -514.371 | 156.3101 | 0 | 0 | 158.1567 | 0 | 0 | -3159.3972 | 0 | 119.4759 | 121.3242 | 63.38% | 60.52% | 82.63% | 99.94% | 99.99%
2018-02 | 100% | 19243.7948 | 16351.3 | -2892.4948 | -15.03% | 1252.6659 | -825.117 | -626.8024 | 392.59 | 0 | 0 | 190.9869 | 0 | 0 | -3276.8183 | 0 | 144.2585 | 135.2342 | 66.15% | 63.43% | 83.04% | 99.95% | 99.99%
2018-03 | 100% | 25113.6512 | 20913.95 | -4199.7012 | -16.72% | -253.342 | -490.1903 | -786.1756 | 404.417 | 0 | -15.315 | 231.9278 | 0 | 0 | -3291.023 | 0 | 182.4427 | 184.0676 | 66.9% | 65.33% | 79.62% | 99.94% | 99.97%
2018-04 | 100% | 30011.3725 | 26152.05 | -3859.3225 | -12.86% | -665.6224 | -105.073 | -955.0402 | 583.1907 | 0 | -35.2757 | 285.7135 | 0 | -51.1215 | -2916.094 | 0 | 224.7627 | 229.5549 | 67.9% | 67.94% | 76.29% | 100% | 100%
2018-05 | 100% | 33583.6188 | 28927.25 | -4656.3688 | -13.87% | -2925.1549 | -659.3419 | -991.9194 | 456.0054 | -150.6101 | -8.2154 | 291.8901 | 0 | -27.1417 | -641.8809 | 0 | 238.9482 | 261.4334 | 70.65% | 72.93% | 74.96% | 99.98% | 100%
2018-06 | 100% | 32634.6477 | 30544.075 | -2090.5727 | -6.406% | -972.0658 | -1416.5276 | -1012.238 | 109.6654 | 0 | 0 | 285.5832 | 0 | 0 | 915.01 | 0 | 256.5297 | 264.1272 | 69.48% | 75.9% | 72.1% | 99.94% | 99.97%
2018-07 | 100% | 29147.3367 | 25793.575 | -3353.7617 | -11.51% | -1530.5749 | -778.3957 | -908.9711 | 369.2499 | 0 | 0 | 232.0913 | 0 | -741.36 | 4.1988 | 0 | 227.5908 | 239.9824 | 66.14% | 72.2% | 70.88% | 99.82% | 99.88%
2018-08 | 100% | 28128.3147 | 26287.1651 | -1841.1495 | -6.546% | -959.2868 | 2409.3752 | -1014.0688 | 588.8339 | 0 | -0.38746 | 238.5516 | 0 | -215.3271 | -2888.8402 | 0 | 222.0792 | 229.6603 | 69.08% | 67.65% | 71.47% | 99.17% | 99.81%
2018-09 | 100% | 24593.3806 | 23438.225 | -1155.1556 | -4.697% | 747.6671 | 1733.3084 | -938.9636 | 538.763 | 0 | -1.5075 | 157.1831 | 0 | -63.1727 | -3328.4334 | 0 | 201.7001 | 195.563 | 67.81% | 65.98% | 73.39% | 98.38% | 99.55%
2018-10 | 100% | 20389.403 | 18740.35 | -1649.053 | -8.088% | 1133.879 | 761.5922 | -782.0354 | 443.2661 | 0 | -1.7167 | 89.7928 | 0 | -41.126 | -3252.705 | 0 | 162.4625 | 153.7877 | 67.32% | 64.21% | 77.37% | 96.87% | 99.32%
2018-11 | 100% | 16928.0896 | 14437.1 | -2490.9896 | -14.72% | 1305.8739 | 77.2115 | -649.6181 | 364.0807 | 0 | 0 | 166.9277 | 0 | -26.7614 | -3728.704 | 0 | 131.0624 | 121.565 | 64.28% | 60.3% | 81.26% | 99.57% | 99.92%
2018-12 | 99.97% | 14142.2191 | 10907.2 | -3235.0191 | -22.87% | 259.0847 | -368.4896 | -503.7338 | 278.8926 | 0 | 0 | 134.6735 | 0 | -11.1524 | -3024.2942 | 0 | 100.1505 | 98.2491 | 63.56% | 59.32% | 84% | 99.9% | 99.98%

## Losses
Month | Soiling measured [kWh] | Soiling budget [kWh] | Snow measured [kWh] | Snow budget [kWh] | Clipping measured [kWh] | Clipping budget [kWh] | Availability measured [kWh] | Availability budget [kWh] | Curtailment measured [kWh] | Curtailment budget [kWh] | Data gaps measured [kWh] | Data gaps budget [kWh]
2016-01 | 482.7933 | 296.6044 | 0 | 0 | 0 | 0 | 8.4003 | 145.3362 | 0 | 0 | 0 | 0
2016-02 | 109.6788 | 442.6111 | 0 | 0 | 1.8657 | 0 | 7.9268 | 216.8794 | 0 | 0 | 18.3139 | 0
2016-03 | 462.8199 | 497.38 | 0 | 0 | 16.9345 | 0 | 2.8264 | 243.7162 | 0 | 0 | 7.3914 | 0
2016-04 | 324.1408 | 523.6578 | 151.5629 | 0 | 74.5617 | 4.4837 | 5.1823 | 256.5475 | 0 | 0 | 0 | 0
2016-05 | 0 | 614.8919 | 169.6265 | 0 | 87.2512 | 10.986 | 0 | 301.1872 | 0 | 0 | 0 | 0
2016-06 | 0 | 572.0528 | 0 | 0 | 0 | 0 | 37.7348 | 280.3059 | 0 | 0 | 0 | 0
2016-07 | 0 | 582.2943 | 0 | 0 | 0 | 0 | 0 | 285.3242 | 0 | 0 | 0 | 0
2016-08 | 0 | 537.09 | 0 | 0 | 3.9251 | 0 | 0 | 263.1741 | 0 | 0 | 0 | 0
2016-09 | 12.4006 | 515.0615 | 0 | 0 | 5.5044 | 0 | 0 | 252.3801 | 0 | 0 | 0 | 0
2016-10 | 237.695 | 423.765 | 0 | 0 | 6.1697 | 0 | 13.9933 | 207.6449 | 0 | 0 | 0 | 0
2016-11 | 469.668 | 360.0837 | 0 | 0 | 0 | 0 | 3.3342 | 176.441 | 0 | 0 | 0 | 0
2016-12 | 394.8514 | 281.1036 | 0 | 0 | 0 | 0 | 0 | 137.7407 | 0 | 0 | 572.9125 | 0
2017-01 | 183.4445 | 303.0778 | 0 | 0 | 0 | 0 | 0 | 148.5081 | 0 | 0 | 780.4935 | 0
2017-02 | 1065.2914 | 320.3063 | 0 | 0 | 0 | 0 | 0 | 156.9501 | 0 | 0 | 0 | 0
2017-03 | 0 | 526.7001 | 109.0104 | 0 | 60.0259 | 0 | 5.8267 | 258.0831 | 0 | 0 | 1627.1212 | 0
2017-04 | 0 | 585.3482 | 0 | 0 | 116.0816 | 5.0119 | 29.7068 | 286.7705 | 0 | 0 | 25.1574 | 0
2017-05 | 0 | 620.1181 | 0 | 0 | 36.7541 | 11.0794 | 0 | 303.7471 | 0 | 0 | 0 | 0
2017-06 | 0 | 595.6982 | 0 | 0 | 4.2238 | 0 | 8.1669 | 291.8921 | 0 | 0 | 0 | 0
2017-07 | 28.769 | 517.0597 | 0 | 0 | 0 | 0 | 0 | 253.3592 | 0 | 0 | 0 | 0
2017-08 | 51.1326 | 521.023 | 0 | 0 | 0 | 0 | 0 | 255.3012 | 0 | 0 | 0 | 0
2017-09 | 0 | 483.9925 | 0 | 0 | 11.4135 | 0 | 0.73285 | 237.1563 | 0 | 0 | 0 | 0
2017-10 | 92.0206 | 486.9964 | 0 | 0 | 2.3852 | 0 | 6107.7789 | 238.6282 | 0 | 0 | 0 | 0
2017-11 | 378.4811 | 350.927 | 0 | 0 | 0 | 0 | 3113.8968 | 171.9542 | 0 | 0 | 6840.2883 | 0
2017-12 | 658.0206 | 344.5931 | 0 | 0 | 0 | 0 | 0 | 168.8506 | 0 | 0 | 1259.6571 | 0
2018-01 | 169.812 | 326.122 | 0 | 0 | 0 | 0 | 1.6431 | 159.7998 | 0 | 0 | 0 | 0
2018-02 | 0 | 392.59 | 0 | 0 | 0 | 0 | 1.3822 | 192.3691 | 0 | 0 | 0 | 0
2018-03 | 81.7496 | 486.1666 | 0 | 0 | 15.315 | 0 | 6.2939 | 238.2216 | 0 | 0 | 0 | 0
2018-04 | 0 | 583.1907 | 0 | 0 | 40.2691 | 4.9934 | 0 | 285.7135 | 0 | 0 | 51.1215 | 0
2018-05 | 142.176 | 598.1815 | 150.6101 | 0 | 18.9028 | 10.6874 | 1.1119 | 293.002 | 0 | 0 | 27.1417 | 0
2018-06 | 492.9695 | 602.6348 | 0 | 0 | 0 | 0 | 9.7078 | 295.2911 | 0 | 0 | 0 | 0
2018-07 | 165.2666 | 534.5165 | 0 | 0 | 0 | 0 | 29.8218 | 261.9131 | 0 | 0 | 741.36 | 0
2018-08 | 0 | 588.8339 | 0 | 0 | 0.38746 | 0 | 49.977 | 288.5286 | 0 | 0 | 215.3271 | 0
2018-09 | 0 | 538.763 | 0 | 0 | 1.5075 | 0 | 106.8108 | 263.9939 | 0 | 0 | 63.1727 | 0
2018-10 | 0 | 443.2661 | 0 | 0 | 1.7167 | 0 | 127.4076 | 217.2004 | 0 | 0 | 41.126 | 0
2018-11 | 0 | 364.0807 | 0 | 0 | 0 | 0 | 11.4719 | 178.3996 | 0 | 0 | 26.7614 | 0
2018-12 | 0 | 278.8926 | 0 | 0 | 0 | 0 | 1.9839 | 136.6574 | 0 | 0 | 11.1524 | 0

## Contract
period | test | basis | measured | guaranteed | guaranteed_effective | pass | shortfall_kwh | damages | bonus | excluded_share | data_share
2015 | availability | time |  | 98% |  | n/a |  |  | 0
2016 | availability | time | 99.95% | 98% |  | PASS | 0 | 0 | 36.9865 | 0%
2017 | availability | time | 95.53% | 98% |  | FAIL | 6562.4381 | 393.7463 | 0 | 0%
2018 | availability | time | 99.46% | 98% |  | PASS | 0 | 0 | 0 | 0%
2015 | performance_ratio | pr_wc |  | 78% | 76% | n/a |  |  | 0 |  | 0%
2016 | performance_ratio | pr_wc | 70.35% | 77.61% | 75.61% | FAIL | 19311.5001 | 1158.69 | 0 |  | 99.7%
2017 | performance_ratio | pr_wc | 67.84% | 77.22% | 75.22% | FAIL | 25669.1799 | 1540.1508 | 0 |  | 93.26%
2018 | performance_ratio | pr_wc | 67.62% | 76.84% | 74.84% | FAIL | 27019.9892 | 1621.1993 | 0 |  | 99.16%
Example clauses only (configs/contract_example.yaml); check against the actual contract.

## QC
check | status | message
clock | ok | labelling offset -0.9 min
clear_days | info | 424 clear days of 929
orientation | ok | fitted tilt 7.0 deg (nominal 5), azimuth 175.3 deg (nominal 180)
level_clearsky | warn | level +22.9% against the clear-sky model on clear days (model uncertainty a few %)
shading | ok | no recurring low-sun shading of the sensor
sensor_soiling | ok | no decline-and-recovery pattern beyond 2.5%
drift | fail | sensor level change from 2017-12-09: -4.0% at most, -1.3% at the end, against the baseline year (3 references)
level_reference | warn | 2016: level +15.9% against poa_ref
level_reference | warn | 2017: level +16.4% against poa_ref
level_reference | warn | 2018: level +16.0% against poa_ref
level_reference | info | POA rescaled by 1/1.160
gaps | info | 2738 daylight intervals filled from the reference

## Downtime
inverter | start | end | hours | energy_kwh | category
INV1 | 2016-01-31 14:00 | 2016-01-31 14:15 | 0.25 | 2.4054 | unlogged
INV1 | 2016-04-09 11:30 | 2016-04-09 11:45 | 0.25 | 3.8187 | unlogged
INV1 | 2016-06-14 07:15 | 2016-06-14 07:30 | 0.25 | 12.763 | unlogged
INV1 | 2016-06-15 07:00 | 2016-06-15 07:15 | 0.25 | 14.1079 | unlogged
INV1 | 2016-10-10 09:30 | 2016-10-10 09:45 | 0.25 | 14.6907 | unlogged
INV1 | 2016-10-26 16:15 | 2016-10-26 16:30 | 0.25 | 1.3882 | unlogged
INV1 | 2017-03-30 15:00 | 2017-03-30 15:15 | 0.25 | 5.6961 | unlogged
INV1 | 2017-04-03 12:00 | 2017-04-03 12:15 | 0.25 | 1.7995 | unlogged
INV1 | 2017-04-06 09:45 | 2017-04-06 10:00 | 0.25 | 20.5245 | unlogged
INV1 | 2017-06-25 17:00 | 2017-06-25 17:15 | 0.25 | 5.817 | unlogged
INV1 | 2017-10-17 06:30 | 2017-10-17 16:30 | 10 | 580.2679 | unlogged
INV1 | 2017-10-18 06:45 | 2017-10-18 16:30 | 9.75 | 336.6523 | unlogged
INV1 | 2017-10-19 06:30 | 2017-10-19 16:30 | 10 | 481.1829 | unlogged
INV1 | 2017-10-20 06:30 | 2017-10-20 16:30 | 10 | 516.4504 | unlogged
INV1 | 2017-10-21 06:30 | 2017-10-21 16:30 | 10 | 557.297 | unlogged
INV1 | 2017-10-22 06:30 | 2017-10-22 16:30 | 10 | 540.1095 | unlogged
INV1 | 2017-10-23 06:30 | 2017-10-23 16:30 | 10 | 554.1853 | unlogged
INV1 | 2017-10-24 06:30 | 2017-10-24 16:30 | 10 | 526.7562 | unlogged
INV1 | 2017-10-25 06:30 | 2017-10-25 16:30 | 10 | 517.4429 | unlogged
INV1 | 2017-10-26 06:30 | 2017-10-26 16:30 | 10 | 518.2909 | unlogged
INV1 | 2017-10-27 06:45 | 2017-10-27 16:30 | 9.75 | 513.6208 | unlogged
INV1 | 2017-10-28 06:45 | 2017-10-28 16:15 | 9.5 | 544.0943 | unlogged
INV1 | 2017-10-29 06:45 | 2017-10-29 16:15 | 9.5 | 504.6152 | unlogged
INV1 | 2017-10-30 06:45 | 2017-10-30 16:15 | 9.5 | 435.8703 | unlogged
INV1 | 2017-10-31 07:00 | 2017-10-31 16:15 | 9.25 | 472.9932 | unlogged
INV1 | 2017-11-01 06:45 | 2017-11-01 16:15 | 9.5 | 475.0228 | unlogged
INV1 | 2017-11-02 06:45 | 2017-11-02 16:15 | 9.5 | 468.6609 | unlogged
INV1 | 2017-11-03 06:45 | 2017-11-03 16:15 | 9.5 | 460.364 | unlogged
INV1 | 2017-11-04 06:45 | 2017-11-04 16:15 | 9.5 | 430.2244 | unlogged
INV1 | 2017-11-05 06:45 | 2017-11-05 16:15 | 9.5 | 498.358 | unlogged
INV1 | 2017-11-06 07:00 | 2017-11-06 16:15 | 9.25 | 397.6606 | unlogged
INV1 | 2017-11-07 07:00 | 2017-11-07 07:30 | 0.5 | 3.8385 | unlogged
INV1 | 2017-11-07 08:00 | 2017-11-07 16:00 | 8 | 470.2148 | unlogged
INV1 | 2017-11-08 06:45 | 2017-11-08 16:00 | 9.25 | 491.473 | unlogged
INV1 | 2017-11-09 06:45 | 2017-11-09 09:00 | 2.25 | 79.5058 | unlogged
INV1 | 2017-11-09 09:15 | 2017-11-09 10:30 | 1.25 | 81.239 | unlogged
INV1 | 2018-06-13 16:45 | 2018-06-13 17:00 | 0.25 | 6.8169 | unlogged
INV1 | 2018-07-11 15:15 | 2018-07-11 15:30 | 0.25 | 7.9657 | unlogged
INV1 | 2018-07-11 15:45 | 2018-07-11 16:00 | 0.25 | 6.2315 | unlogged
INV1 | 2018-08-05 05:15 | 2018-08-05 05:30 | 0.25 | 1.572 | unlogged
INV1 | 2018-08-06 05:00 | 2018-08-06 05:30 | 0.5 | 2.9518 | unlogged
INV1 | 2018-08-06 05:45 | 2018-08-06 06:00 | 0.25 | 1.4764 | unlogged
INV1 | 2018-08-07 05:15 | 2018-08-07 05:30 | 0.25 | 1.4208 | unlogged
INV1 | 2018-08-07 05:45 | 2018-08-07 06:00 | 0.25 | 1.4218 | unlogged
INV1 | 2018-08-09 05:00 | 2018-08-09 05:45 | 0.75 | 3.9055 | unlogged
INV1 | 2018-08-23 06:00 | 2018-08-23 06:15 | 0.25 | 5.2085 | unlogged
INV1 | 2018-08-24 06:00 | 2018-08-24 06:15 | 0.25 | 5.2012 | unlogged
INV1 | 2018-08-27 06:00 | 2018-08-27 06:15 | 0.25 | 5.3889 | unlogged
INV1 | 2018-08-28 06:15 | 2018-08-28 06:30 | 0.25 | 5.3986 | unlogged
INV1 | 2018-08-31 06:00 | 2018-08-31 06:15 | 0.25 | 4.9555 | unlogged
INV1 | 2018-09-04 06:00 | 2018-09-04 06:30 | 0.5 | 10.4024 | unlogged
INV1 | 2018-09-07 06:00 | 2018-09-07 06:15 | 0.25 | 4.431 | unlogged
INV1 | 2018-09-11 06:15 | 2018-09-11 06:30 | 0.25 | 4.9906 | unlogged
INV1 | 2018-09-13 06:15 | 2018-09-13 06:30 | 0.25 | 4.7289 | unlogged
INV1 | 2018-09-17 06:15 | 2018-09-17 06:45 | 0.5 | 8.7805 | unlogged
INV1 | 2018-09-20 06:00 | 2018-09-20 06:30 | 0.5 | 7.9361 | unlogged
INV1 | 2018-09-21 06:00 | 2018-09-21 06:15 | 0.25 | 4.3011 | unlogged
INV1 | 2018-09-23 06:00 | 2018-09-23 06:30 | 0.5 | 6.9925 | unlogged
INV1 | 2018-09-25 06:00 | 2018-09-25 06:45 | 0.75 | 11.9483 | unlogged
INV1 | 2018-09-26 06:00 | 2018-09-26 06:15 | 0.25 | 4.0681 | unlogged
INV1 | 2018-09-27 06:15 | 2018-09-27 06:30 | 0.25 | 3.7708 | unlogged
INV1 | 2018-09-28 06:15 | 2018-09-28 06:30 | 0.25 | 3.9418 | unlogged
INV1 | 2018-09-29 06:15 | 2018-09-29 06:30 | 0.25 | 3.6695 | unlogged
INV1 | 2018-09-30 06:30 | 2018-09-30 07:00 | 0.5 | 7.0961 | unlogged
INV1 | 2018-10-02 06:15 | 2018-10-02 06:30 | 0.25 | 2.5274 | unlogged
INV1 | 2018-10-04 06:15 | 2018-10-04 06:45 | 0.5 | 7.475 | unlogged
INV1 | 2018-10-05 06:00 | 2018-10-05 06:15 | 0.25 | 3.4426 | unlogged
INV1 | 2018-10-06 06:30 | 2018-10-06 06:45 | 0.25 | 2.5189 | unlogged
INV1 | 2018-10-09 06:00 | 2018-10-09 06:15 | 0.25 | 3.0372 | unlogged
INV1 | 2018-10-10 06:00 | 2018-10-10 06:15 | 0.25 | 3.3461 | unlogged
INV1 | 2018-10-10 06:45 | 2018-10-10 07:00 | 0.25 | 3.3461 | unlogged
INV1 | 2018-10-12 06:00 | 2018-10-12 06:15 | 0.25 | 2.9125 | unlogged
INV1 | 2018-10-12 06:45 | 2018-10-12 07:00 | 0.25 | 2.9125 | unlogged
INV1 | 2018-10-14 17:30 | 2018-10-14 17:45 | 0.25 | 1.5311 | unlogged
INV1 | 2018-10-15 06:15 | 2018-10-15 06:30 | 0.25 | 3.3261 | unlogged
INV1 | 2018-10-16 06:00 | 2018-10-16 06:15 | 0.25 | 2.637 | unlogged
INV1 | 2018-10-17 06:00 | 2018-10-17 06:15 | 0.25 | 2.9453 | unlogged
INV1 | 2018-10-17 06:45 | 2018-10-17 07:00 | 0.25 | 2.9453 | unlogged
INV1 | 2018-10-20 06:00 | 2018-10-20 06:30 | 0.5 | 5.6406 | unlogged
INV1 | 2018-10-21 06:15 | 2018-10-21 06:30 | 0.25 | 1.7028 | unlogged
INV1 | 2018-10-22 06:45 | 2018-10-22 07:15 | 0.5 | 10.132 | unlogged
INV1 | 2018-10-23 06:30 | 2018-10-23 07:00 | 0.5 | 4.6822 | unlogged
INV1 | 2018-10-25 06:00 | 2018-10-25 06:15 | 0.25 | 2.1199 | unlogged
INV1 | 2018-10-25 06:30 | 2018-10-25 06:45 | 0.25 | 2.395 | unlogged
INV1 | 2018-10-26 06:00 | 2018-10-26 06:15 | 0.25 | 1.9993 | unlogged
INV1 | 2018-10-27 06:00 | 2018-10-27 07:00 | 1 | 7.6423 | unlogged
INV1 | 2018-10-28 06:00 | 2018-10-28 06:15 | 0.25 | 1.7764 | unlogged
INV1 | 2018-10-28 07:00 | 2018-10-28 07:15 | 0.25 | 6.9393 | unlogged
INV1 | 2018-10-29 06:00 | 2018-10-29 06:15 | 0.25 | 1.7137 | unlogged
INV1 | 2018-10-29 06:30 | 2018-10-29 06:45 | 0.25 | 1.7137 | unlogged
INV1 | 2018-10-30 06:00 | 2018-10-30 07:00 | 1 | 7.0339 | unlogged
INV1 | 2018-10-31 06:00 | 2018-10-31 06:15 | 0.25 | 1.8579 | unlogged
INV1 | 2018-11-02 06:15 | 2018-11-02 06:45 | 0.5 | 3.3781 | unlogged
INV1 | 2018-11-03 06:15 | 2018-11-03 06:30 | 0.25 | 1.5405 | unlogged
INV1 | 2018-11-28 15:30 | 2018-11-28 15:45 | 0.25 | 2.6921 | unlogged
INV1 | 2018-12-25 07:15 | 2018-12-25 07:30 | 0.25 | 1.8424 | unlogged
INV2 | 2016-01-08 15:45 | 2016-01-08 16:00 | 0.25 | 0.92907 | unlogged
INV2 | 2016-01-25 09:45 | 2016-01-25 10:00 | 0.25 | 5.7265 | unlogged
INV2 | 2016-01-26 16:15 | 2016-01-26 16:30 | 0.25 | 0.78379 | unlogged
INV2 | 2016-01-28 16:15 | 2016-01-28 16:30 | 0.25 | 0.96379 | unlogged
INV2 | 2016-02-18 12:30 | 2016-02-18 12:45 | 0.25 | 8.5978 | unlogged
INV2 | 2016-02-18 16:45 | 2016-02-18 17:00 | 0.25 | 1.0749 | unlogged
INV2 | 2016-03-25 16:15 | 2016-03-25 16:30 | 0.25 | 2.9897 | unlogged
INV2 | 2016-04-09 11:30 | 2016-04-09 11:45 | 0.25 | 1.4504 | unlogged
INV2 | 2016-06-14 07:15 | 2016-06-14 07:30 | 0.25 | 4.8954 | unlogged
INV2 | 2016-06-15 07:00 | 2016-06-15 07:15 | 0.25 | 5.4142 | unlogged
INV2 | 2016-11-03 16:00 | 2016-11-03 16:15 | 0.25 | 0.9208 | unlogged
INV2 | 2016-11-04 16:00 | 2016-11-04 16:15 | 0.25 | 0.6884 | unlogged
INV2 | 2016-11-14 15:45 | 2016-11-14 16:00 | 0.25 | 0.99763 | unlogged
INV2 | 2016-11-17 15:45 | 2016-11-17 16:00 | 0.25 | 0.79421 | unlogged
INV2 | 2016-11-18 15:45 | 2016-11-18 16:00 | 0.25 | 0.65985 | unlogged
INV2 | 2017-03-03 17:00 | 2017-03-03 17:15 | 0.25 | 0.81397 | unlogged
INV2 | 2017-04-03 12:00 | 2017-04-03 12:15 | 0.25 | 0.67399 | unlogged
INV2 | 2017-04-06 09:45 | 2017-04-06 10:00 | 0.25 | 7.8927 | unlogged
INV2 | 2017-06-25 17:00 | 2017-06-25 17:15 | 0.25 | 2.2192 | unlogged
INV2 | 2017-09-12 17:00 | 2017-09-12 17:15 | 0.25 | 0.78037 | unlogged
INV2 | 2017-10-23 16:15 | 2017-10-23 16:30 | 0.25 | 0.86826 | unlogged
INV2 | 2017-10-24 16:15 | 2017-10-24 16:30 | 0.25 | 0.8271 | unlogged
INV2 | 2017-10-25 16:15 | 2017-10-25 16:30 | 0.25 | 0.67857 | unlogged
INV2 | 2017-10-26 16:15 | 2017-10-26 16:30 | 0.25 | 0.75164 | unlogged
INV2 | 2017-11-04 16:00 | 2017-11-04 16:15 | 0.25 | 0.72445 | unlogged
INV2 | 2017-11-06 16:00 | 2017-11-06 16:15 | 0.25 | 0.77731 | unlogged
INV2 | 2017-11-14 15:45 | 2017-11-14 16:00 | 0.25 | 0.75325 | unlogged
INV2 | 2018-01-26 16:15 | 2018-01-26 16:30 | 0.25 | 0.82396 | unlogged
INV2 | 2018-01-28 16:15 | 2018-01-28 16:30 | 0.25 | 1.2138 | unlogged
INV2 | 2018-02-15 16:45 | 2018-02-15 17:00 | 0.25 | 0.84124 | unlogged
INV2 | 2018-02-26 16:45 | 2018-02-26 17:00 | 0.25 | 0.81781 | unlogged
INV2 | 2018-03-14 16:15 | 2018-03-14 16:30 | 0.25 | 2.7858 | unlogged
INV2 | 2018-03-15 16:00 | 2018-03-15 16:15 | 0.25 | 3.382 | unlogged
INV2 | 2018-03-15 17:00 | 2018-03-15 17:15 | 0.25 | 1.1113 | unlogged
INV2 | 2018-05-08 16:30 | 2018-05-08 16:45 | 0.25 | 1.1362 | unlogged
INV2 | 2018-06-13 16:45 | 2018-06-13 17:00 | 0.25 | 2.6041 | unlogged
INV2 | 2018-07-11 15:15 | 2018-07-11 16:00 | 0.75 | 7.8039 | unlogged
INV2 | 2018-07-11 17:15 | 2018-07-11 17:30 | 0.25 | 3.3623 | unlogged
INV2 | 2018-07-19 15:00 | 2018-07-19 15:15 | 0.25 | 4.4507 | unlogged
INV2 | 2018-08-05 06:00 | 2018-08-05 06:15 | 0.25 | 2.4109 | unlogged
INV2 | 2018-08-20 06:15 | 2018-08-20 06:30 | 0.25 | 2.2465 | unlogged
INV2 | 2018-08-23 06:00 | 2018-08-23 06:15 | 0.25 | 1.9851 | unlogged
INV2 | 2018-08-24 06:00 | 2018-08-24 06:15 | 0.25 | 1.9823 | unlogged
INV2 | 2018-08-27 06:00 | 2018-08-27 06:15 | 0.25 | 2.0545 | unlogged
INV2 | 2018-08-28 06:15 | 2018-08-28 06:30 | 0.25 | 2.0582 | unlogged
INV2 | 2018-08-31 06:00 | 2018-08-31 06:30 | 0.5 | 3.7754 | unlogged
INV2 | 2018-09-04 06:00 | 2018-09-04 06:30 | 0.5 | 3.9645 | unlogged
INV2 | 2018-09-07 06:00 | 2018-09-07 06:15 | 0.25 | 1.6859 | unlogged
INV2 | 2018-09-11 06:15 | 2018-09-11 06:30 | 0.25 | 1.9012 | unlogged
INV2 | 2018-09-13 06:15 | 2018-09-13 06:30 | 0.25 | 1.8005 | unlogged
INV2 | 2018-09-16 06:30 | 2018-09-16 06:45 | 0.25 | 1.7148 | unlogged
INV2 | 2018-09-17 06:15 | 2018-09-17 06:45 | 0.5 | 3.3405 | unlogged
INV2 | 2018-09-20 06:00 | 2018-09-20 06:30 | 0.5 | 3.0157 | unlogged
INV2 | 2018-09-21 06:00 | 2018-09-21 06:15 | 0.25 | 1.636 | unlogged
INV2 | 2018-09-23 06:00 | 2018-09-23 06:30 | 0.5 | 2.6528 | unlogged
INV2 | 2018-09-25 06:00 | 2018-09-25 06:45 | 0.75 | 4.5405 | unlogged
INV2 | 2018-09-26 06:00 | 2018-09-26 06:15 | 0.25 | 1.5463 | unlogged
INV2 | 2018-09-27 06:15 | 2018-09-27 06:30 | 0.25 | 1.432 | unlogged
INV2 | 2018-09-28 06:15 | 2018-09-28 06:30 | 0.25 | 1.4977 | unlogged
INV2 | 2018-09-29 06:15 | 2018-09-29 06:30 | 0.25 | 1.393 | unlogged
INV2 | 2018-09-30 06:30 | 2018-09-30 07:00 | 0.5 | 2.6926 | unlogged
INV2 | 2018-10-02 06:15 | 2018-10-02 06:30 | 0.25 | 0.95382 | unlogged
INV2 | 2018-10-02 17:30 | 2018-10-02 17:45 | 0.25 | 0.67687 | unlogged
INV2 | 2018-10-03 06:45 | 2018-10-03 07:00 | 0.25 | 1.1738 | unlogged
INV2 | 2018-10-04 06:15 | 2018-10-04 06:45 | 0.5 | 2.8383 | unlogged
INV2 | 2018-10-05 06:00 | 2018-10-05 06:15 | 0.25 | 1.3057 | unlogged
INV2 | 2018-10-06 06:30 | 2018-10-06 06:45 | 0.25 | 0.95053 | unlogged
INV2 | 2018-10-09 06:00 | 2018-10-09 06:15 | 0.25 | 1.1498 | unlogged
INV2 | 2018-10-10 06:00 | 2018-10-10 06:15 | 0.25 | 1.2686 | unlogged
INV2 | 2018-10-10 06:45 | 2018-10-10 07:00 | 0.25 | 1.2686 | unlogged
INV2 | 2018-10-12 06:00 | 2018-10-12 06:15 | 0.25 | 1.1019 | unlogged
INV2 | 2018-10-12 06:45 | 2018-10-12 07:00 | 0.25 | 1.1019 | unlogged
INV2 | 2018-10-15 06:15 | 2018-10-15 06:30 | 0.25 | 1.261 | unlogged
INV2 | 2018-10-15 17:30 | 2018-10-15 17:45 | 0.25 | 0.65552 | unlogged
INV2 | 2018-10-16 06:00 | 2018-10-16 06:15 | 0.25 | 0.99597 | unlogged
INV2 | 2018-10-17 06:00 | 2018-10-17 06:15 | 0.25 | 1.1145 | unlogged
INV2 | 2018-10-17 06:45 | 2018-10-17 07:00 | 0.25 | 1.1145 | unlogged
INV2 | 2018-10-20 06:00 | 2018-10-20 06:30 | 0.5 | 2.1328 | unlogged
INV2 | 2018-10-21 06:15 | 2018-10-21 06:30 | 0.25 | 0.63681 | unlogged
INV2 | 2018-10-22 06:45 | 2018-10-22 07:15 | 0.5 | 3.8614 | unlogged
INV2 | 2018-10-23 06:30 | 2018-10-23 07:00 | 0.5 | 1.7644 | unlogged
INV2 | 2018-10-23 07:15 | 2018-10-23 07:30 | 0.25 | 2.9848 | unlogged
INV2 | 2018-10-25 06:00 | 2018-10-25 06:15 | 0.25 | 0.79714 | unlogged
INV2 | 2018-10-25 06:30 | 2018-10-25 06:45 | 0.25 | 0.90289 | unlogged
INV2 | 2018-10-26 06:00 | 2018-10-26 06:15 | 0.25 | 0.75079 | unlogged
INV2 | 2018-10-26 17:15 | 2018-10-26 17:30 | 0.25 | 0.7464 | unlogged
INV2 | 2018-10-27 06:00 | 2018-10-27 07:00 | 1 | 2.8667 | unlogged
INV2 | 2018-10-28 06:00 | 2018-10-28 06:15 | 0.25 | 0.66509 | unlogged
INV2 | 2018-10-28 07:00 | 2018-10-28 07:15 | 0.25 | 2.6512 | unlogged
INV2 | 2018-10-29 06:00 | 2018-10-29 06:15 | 0.25 | 0.64101 | unlogged
INV2 | 2018-10-29 06:30 | 2018-10-29 06:45 | 0.25 | 0.64101 | unlogged
INV2 | 2018-10-29 07:00 | 2018-10-29 07:15 | 0.25 | 2.7627 | unlogged
INV2 | 2018-10-30 06:00 | 2018-10-30 07:00 | 1 | 2.6328 | unlogged
INV2 | 2018-10-31 06:00 | 2018-10-31 06:15 | 0.25 | 0.69644 | unlogged
INV2 | 2018-11-02 06:15 | 2018-11-02 06:45 | 0.5 | 1.2631 | unlogged
INV2 | 2018-11-02 07:15 | 2018-11-02 07:30 | 0.25 | 2.7713 | unlogged
INV2 | 2018-11-28 15:30 | 2018-11-28 15:45 | 0.25 | 1.0171 | unlogged
INV2 | 2018-11-29 12:15 | 2018-11-29 12:30 | 0.25 | 1.1156 | unlogged
INV2 | 2018-11-29 13:00 | 2018-11-29 13:15 | 0.25 | 0.64834 | unlogged
INV2 | 2018-12-25 07:15 | 2018-12-25 07:30 | 0.25 | 0.69046 | unlogged