## Summary
Plant | PVDAQ-34 (building A)
DC / AC [kW] | 146.6 / 135.0
Location | 36.1952, -115.1582
Report time zone | Etc/GMT+8
Months | 2016-01 .. 2018-12
Budget P50 [kWh] | 779016.1716
Actual [kWh] | 664362.873
Deviation [%] | -14.72%
Bridge method | sequential
Unexplained residual [kWh] | -45751.3969
YoY performance trend [%/yr] | 0.1509%
QC findings (warn/fail) | 4
Note | Working material. PR definitions follow public descriptions of IEC 61724-1 and NREL weather-corrected PR; not a certified implementation. Contract clauses are examples.

## Bridge
Month | Coverage | Budget P50 [kWh] | Actual [kWh] | Deviation [kWh] | Deviation [%] | Irradiance [kWh] | Temperature [kWh] | Degradation [kWh] | Soiling [kWh] | Snow [kWh] | Clipping [kWh] | Availability [kWh] | Curtailment [kWh] | Data gaps [kWh] | Unexplained [kWh] | Check [kWh] | POA actual [kWh/m2] | POA budget [kWh/m2] | PR | PR weather-corr. | PR budget | Availability time | Availability energy
2016-01 | 100% | 16562.0649 | 11739.675 | -4822.3899 | -29.12% | -3465.4256 | -1.2874 | -349.9807 | 159.9746 | 0 | 0 | 124.6212 | 0 | 0 | -1290.2919 | 0 | 109.6186 | 138.1569 | 73.03% | 68.17% | 81.75% | 99.9% | 99.96%
2016-02 | 100% | 17995.7968 | 17187.825 | -807.9718 | -4.49% | 2355.384 | -824.1215 | -529.5261 | 319.2826 | 0 | 0 | 172.0588 | 0 | -24.2547 | -2276.7949 | 2.2737e-13 | 168.7095 | 149.0296 | 69.48% | 66.97% | 82.35% | 99.91% | 99.88%
2016-03 | 100% | 22610.3628 | 20446.2 | -2164.1628 | -9.572% | -69.4112 | -596.8438 | -603.965 | 168.9991 | 0 | -0.39907 | 215.557 | 0 | -9.11 | -1268.9897 | 0 | 194.4634 | 194.9096 | 71.7% | 70.66% | 79.11% | 100% | 100%
2016-04 | 100% | 26280.4081 | 21634.875 | -4645.5331 | -17.68% | -3566.5246 | 391.674 | -645.0584 | 269.5363 | -122.3752 | -10.4593 | 222.4339 | 0 | 0 | -1184.7598 | 0 | 204.3326 | 235.8961 | 72.2% | 70.99% | 75.97% | 99.93% | 99.98%
2016-05 | 100% | 28739.7611 | 25516.45 | -3223.3111 | -11.22% | -1676.5922 | 64.5763 | -768.5468 | 482.2726 | -141.3057 | -15.8596 | 266.2545 | 0 | 0 | -1434.1102 | 0 | 247.0378 | 262.0517 | 70.44% | 71.12% | 74.79% | 100% | 100%
2016-06 | 100% | 27625.5641 | 2573.4 | -25052.1641 | -90.68% | -974.0086 | -1422.9885 | -724.734 | 283.6324 | 0 | 0 | -9607.8198 | 0 | -10896.6888 | -1709.5568 | 0 | 252.8705 | 261.7603 | 6.94% | 7.628% | 71.97% | 20.98% | 20.71%
2016-07 | 100% | 24813.2369 | 18891.25 | -5921.9869 | -23.87% | 2009.5385 | -1130.6608 | -748.4332 | 80.5151 | 0 | 0 | 226.5803 | 0 | -6316.3339 | -43.1929 | 0 | 258.9715 | 239.3475 | 49.75% | 54.95% | 70.7% | 99.92% | 99.87%
2016-08 | 100% | 24435.3945 | 22920.975 | -1514.4195 | -6.198% | -164.1263 | -555.2307 | -700.8251 | -44.209 | 0 | 0 | 232.4769 | 0 | 0 | -282.5053 | 0 | 232.8184 | 234.0524 | 67.14% | 72.45% | 71.2% | 100% | 100%
2016-09 | 100% | 21940.8132 | 21075.325 | -865.4882 | -3.945% | 714.3256 | 110.6394 | -681.8898 | -25.3287 | 0 | -0.9678 | 223.0696 | 0 | 0 | -1205.3364 | 1.1369e-13 | 212.2002 | 205.248 | 67.73% | 69.84% | 72.9% | 100% | 100%
2016-10 | 100% | 18785.9574 | 16715.025 | -2070.9324 | -11.02% | -310.8921 | 285.5884 | -569.2631 | -42.9868 | 0 | -0.13461 | 163.7223 | 0 | 0 | -1596.9664 | 0 | 164.4324 | 166.9284 | 69.32% | 67.59% | 76.75% | 99.76% | 99.88%
2016-11 | 100% | 16183.2061 | 13933.825 | -2249.3811 | -13.9% | -29.3432 | -198.1553 | -490.8266 | -74.8574 | 0 | 0 | 156.2109 | 0 | 0 | -1612.4096 | 0 | 137.0885 | 137.1174 | 69.31% | 66.4% | 80.49% | 100% | 100%
2016-12 | 100% | 13701.026 | 10600.9 | -3100.126 | -22.63% | -1530.3922 | 301.5694 | -388.624 | 4.3108 | 0 | 0 | 105.5375 | 0 | 0 | -1592.5277 | 0 | 100.0995 | 112.3583 | 72.22% | 64.87% | 83.16% | 99.89% | 99.84%
2017-01 | 100% | 16562.0649 | 12243.675 | -4318.3899 | -26.07% | -3129.0444 | 14.5929 | -425.0671 | 102.4869 | 0 | 0 | 131.5409 | 0 | 0 | -1012.8991 | 0 | 112.4041 | 138.1569 | 74.28% | 69.26% | 81.75% | 100% | 100%
2017-02 | 100% | 17995.7968 | 12943.125 | -5052.6718 | -28.08% | -3686.093 | -94.9633 | -454.6887 | -639.2812 | 0 | 0 | 138.9904 | 0 | 0 | -316.6361 | 0 | 118.9612 | 149.0296 | 74.2% | 69.31% | 82.35% | 100% | 100%
2017-03 | 100% | 22610.3628 | 20867.275 | -1743.0878 | -7.709% | 586.807 | 162.31 | -756.1565 | 336.5856 | 0 | -9.2119 | 214.5009 | 0 | -10.6222 | -2267.3006 | 2.2737e-13 | 200.0753 | 194.9096 | 71.12% | 68% | 79.11% | 99.7% | 99.93%
2017-04 | 100% | 26280.4081 | 24185.25 | -2095.1581 | -7.972% | -612.2814 | 287.3826 | -850.8871 | 179.0903 | 0 | -17.336 | 251.5223 | 0 | 0 | -1332.6488 | 0 | 230.6928 | 235.8961 | 71.49% | 70.66% | 75.97% | 99.93% | 99.99%
2017-05 | 100% | 28739.7611 | 25916.475 | -2823.2861 | -9.824% | -765.5533 | -480.9806 | -912.2249 | 0.34516 | 0 | -5.0696 | 268.495 | 0 | 0 | -928.2979 | 0 | 255.2805 | 262.0517 | 69.23% | 71.15% | 74.79% | 100% | 100%
2017-06 | 100% | 27625.5641 | 25240 | -2385.5641 | -8.635% | 122.1297 | -1342.5207 | -886.7932 | -48.1466 | 0 | -1.1647 | 226.6891 | 0 | 0 | -455.7577 | 0 | 263.1669 | 261.7603 | 65.4% | 71.56% | 71.97% | 99.87% | 99.88%
2017-07 | 100% | 24813.2369 | 22369.775 | -2443.4619 | -9.847% | -948.9081 | -929.4212 | -779.4074 | 46.7393 | 0 | 0 | 223.7929 | 0 | 0 | -56.2574 | 0 | 230.5299 | 239.3475 | 66.17% | 72.86% | 70.7% | 100% | 100%
2017-08 | 100% | 24435.3945 | 22373.075 | -2062.3195 | -8.44% | -711.0957 | -602.6489 | -795.3417 | 369.9029 | 0 | 0 | 225.5183 | 0 | 0 | -548.6542 | 0 | 227.6169 | 234.0524 | 67.03% | 72.49% | 71.2% | 100% | 100%
2017-09 | 100% | 21940.8132 | 20055.725 | -1885.0882 | -8.592% | -768.8439 | 333.2522 | -748.6482 | 217.3233 | 0 | 0 | 209.6624 | 0 | 0 | -1127.834 | 0 | 198.3845 | 205.248 | 68.94% | 70.4% | 72.9% | 100% | 100%
2017-10 | 100% | 18785.9574 | 18923.225 | 137.2676 | 0.7307% | 2740.0949 | 131.5939 | -762.3112 | 80.0638 | 0 | 0 | 211.064 | 0 | 0 | -2263.2378 | 0 | 191.3691 | 166.9284 | 67.43% | 66.31% | 76.75% | 100% | 100%
2017-11 | 100% | 16183.2061 | 13188.275 | -2994.9311 | -18.51% | -819.0861 | 268.8011 | -556.6256 | -38.3168 | 0 | 0 | 150.2452 | 0 | 0 | -1999.949 | 0 | 130.4538 | 137.1174 | 68.94% | 64.3% | 80.49% | 99.91% | 99.98%
2017-12 | 100% | 13701.026 | 12485.675 | -1215.351 | -8.871% | 1164.2537 | 190.0082 | -542.0982 | -71.8926 | 0 | 0 | 146.5979 | 0 | 0 | -2102.2201 | 0 | 121.9234 | 112.3583 | 69.83% | 63.39% | 83.16% | 100% | 100%
2018-01 | 100% | 16562.0649 | 12545.875 | -4016.1899 | -24.25% | -2142.7766 | -332.7184 | -513.4309 | 124.1151 | 0 | 0 | 137.1024 | 0 | 0 | -1288.4815 | 0 | 120.541 | 138.1569 | 70.98% | 67.64% | 81.75% | 100% | 100%
2018-02 | 100% | 17995.7968 | 15368.25 | -2627.5468 | -14.6% | -373.9889 | -589.7972 | -627.1208 | -73.2416 | 0 | 0 | 165.706 | 0 | 0 | -1129.1042 | 0 | 146.1824 | 149.0296 | 71.69% | 68.65% | 82.35% | 100% | 100%
2018-03 | 100% | 22610.3628 | 19941.55 | -2668.8128 | -11.8% | -1085.1394 | -337.3562 | -788.4893 | 177.368 | 0 | -0.96195 | 202.6678 | 0 | 0 | -836.9018 | 0 | 185.7863 | 194.9096 | 73.2% | 71.42% | 79.11% | 99.92% | 99.98%
2018-04 | 100% | 26280.4081 | 23794.45 | -2485.9581 | -9.459% | -781.1359 | -50.006 | -957.2397 | 364.1092 | 0 | -2.491 | 247.3942 | 0 | 0 | -1306.589 | 0 | 229.1696 | 235.8961 | 70.81% | 70.81% | 75.97% | 100% | 100%
2018-05 | 100% | 28739.7611 | 24837.8 | -3901.9611 | -13.58% | -1894.7021 | -609.4461 | -997.3528 | 431.8339 | -122.6576 | -5.3903 | 254.9319 | 0 | -13.0458 | -946.1323 | 0 | 245.0437 | 262.0517 | 69.12% | 71.38% | 74.79% | 100% | 100%
2018-06 | 100% | 27625.5641 | 25652.275 | -1973.2891 | -7.143% | 189.9295 | -1321.6386 | -1017.7537 | 239.9705 | 0 | 0 | 257.3344 | 0 | 0 | -321.1311 | 0 | 263.8059 | 261.7603 | 66.31% | 72.5% | 71.97% | 100% | 100%
2018-07 | 100% | 24813.2369 | 21628.55 | -3184.6869 | -12.83% | -991.9093 | -927.6241 | -888.5357 | 316.0174 | 0 | 0 | 212.7143 | 0 | -630.151 | -275.1987 | 0 | 230.1217 | 239.3475 | 64.09% | 70.57% | 70.7% | 99.93% | 99.96%
2018-08 | 100% | 24435.3945 | 22796.198 | -1639.1965 | -6.708% | -280.5623 | 2083.2179 | -1029.274 | 308.1359 | 0 | 0 | 221.0393 | 0 | -31.7572 | -2909.9961 | -2.2737e-13 | 231.6233 | 234.0524 | 67.12% | 65.91% | 71.2% | 99.53% | 99.85%
2018-09 | 100% | 21940.8132 | 20868.7 | -1072.1132 | -4.886% | 563.6829 | 1556.2148 | -953.3547 | 123.7457 | 0 | 0 | 140.6936 | 0 | 0 | -2503.0955 | -2.2737e-13 | 210.7147 | 205.248 | 67.54% | 65.88% | 72.9% | 98.41% | 99.56%
2018-10 | 100% | 18785.9574 | 17737.625 | -1048.3324 | -5.58% | 300.4814 | 744.3134 | -793.8745 | -10.116 | 0 | 0 | 68.7383 | 0 | 0 | -1357.8749 | 0 | 169.7414 | 166.9284 | 71.26% | 68.08% | 76.75% | 96.92% | 99.31%
2018-11 | 100% | 16183.2061 | 14085.925 | -2097.2811 | -12.96% | -32.0584 | 160.006 | -659.204 | 14.6945 | 0 | 0 | 144.7326 | 0 | 0 | -1725.4518 | 0 | 136.9984 | 137.1174 | 70.12% | 65.84% | 80.49% | 99.44% | 99.91%
2018-12 | 99.97% | 13696.4222 | 11078.4 | -2618.0222 | -19.11% | -965.3585 | -237.9812 | -510.123 | 218.8902 | 0 | 0 | 118.8559 | 0 | 0 | -1242.3056 | 0 | 104.554 | 112.3205 | 72.26% | 67.47% | 83.16% | 99.9% | 99.98%

## Losses
Month | Soiling measured [kWh] | Soiling budget [kWh] | Snow measured [kWh] | Snow budget [kWh] | Clipping measured [kWh] | Clipping budget [kWh] | Availability measured [kWh] | Availability budget [kWh] | Curtailment measured [kWh] | Curtailment budget [kWh] | Data gaps measured [kWh] | Data gaps budget [kWh]
2016-01 | 102.7624 | 262.737 | 0 | 0 | 0 | 0 | 4.1199 | 128.7411 | 0 | 0 | 0 | 0
2016-02 | 72.3384 | 391.621 | 0 | 0 | 0 | 0 | 19.8355 | 191.8943 | 0 | 0 | 24.2547 | 0
2016-03 | 270.9131 | 439.9122 | 0 | 0 | 0.39907 | 0 | 0 | 215.557 | 0 | 0 | 9.11 | 0
2016-04 | 193.4713 | 463.0076 | 122.3752 | 0 | 10.4593 | 0 | 4.4398 | 226.8737 | 0 | 0 | 0 | 0
2016-05 | 61.104 | 543.3766 | 141.3057 | 0 | 15.8596 | 0 | 0 | 266.2545 | 0 | 0 | 0 | 0
2016-06 | 221.4971 | 505.1295 | 0 | 0 | 0 | 0 | 9855.3333 | 247.5135 | 0 | 0 | 10896.6888 | 0
2016-07 | 433.6815 | 514.1967 | 0 | 0 | 0 | 0 | 25.3761 | 251.9564 | 0 | 0 | 6316.3339 | 0
2016-08 | 518.6517 | 474.4426 | 0 | 0 | 0 | 0 | 0 | 232.4769 | 0 | 0 | 0 | 0
2016-09 | 480.5728 | 455.244 | 0 | 0 | 0.9678 | 0 | 0 | 223.0696 | 0 | 0 | 0 | 0
2016-10 | 417.9897 | 375.0029 | 0 | 0 | 0.13461 | 0 | 20.0291 | 183.7514 | 0 | 0 | 0 | 0
2016-11 | 393.6552 | 318.7978 | 0 | 0 | 0 | 0 | 0 | 156.2109 | 0 | 0 | 0 | 0
2016-12 | 244.7838 | 249.0946 | 0 | 0 | 0 | 0 | 16.5188 | 122.0564 | 0 | 0 | 0 | 0
2017-01 | 165.9639 | 268.4508 | 0 | 0 | 0 | 0 | 0 | 131.5409 | 0 | 0 | 0 | 0
2017-02 | 922.9351 | 283.6539 | 0 | 0 | 0 | 0 | 0 | 138.9904 | 0 | 0 | 0 | 0
2017-03 | 129.3663 | 465.9518 | 0 | 0 | 9.2119 | 0 | 13.8155 | 228.3164 | 0 | 0 | 10.6222 | 0
2017-04 | 338.4241 | 517.5144 | 0 | 0 | 17.336 | 0 | 2.0597 | 253.582 | 0 | 0 | 0 | 0
2017-05 | 547.6038 | 547.9489 | 0 | 0 | 5.0696 | 0 | 0 | 268.495 | 0 | 0 | 0 | 0
2017-06 | 574.1903 | 526.0437 | 0 | 0 | 1.1647 | 0 | 31.0723 | 257.7614 | 0 | 0 | 0 | 0
2017-07 | 409.981 | 456.7203 | 0 | 0 | 0 | 0 | 0 | 223.7929 | 0 | 0 | 0 | 0
2017-08 | 90.3385 | 460.2414 | 0 | 0 | 0 | 0 | 0 | 225.5183 | 0 | 0 | 0 | 0
2017-09 | 210.559 | 427.8824 | 0 | 0 | 0 | 0 | 0 | 209.6624 | 0 | 0 | 0 | 0
2017-10 | 350.679 | 430.7428 | 0 | 0 | 0 | 0 | 0 | 211.064 | 0 | 0 | 0 | 0
2017-11 | 349.1042 | 310.7874 | 0 | 0 | 0 | 0 | 2.0406 | 152.2858 | 0 | 0 | 0 | 0
2017-12 | 371.0719 | 299.1793 | 0 | 0 | 0 | 0 | 0 | 146.5979 | 0 | 0 | 0 | 0
2018-01 | 155.6857 | 279.8008 | 0 | 0 | 0 | 0 | 0 | 137.1024 | 0 | 0 | 0 | 0
2018-02 | 411.4171 | 338.1754 | 0 | 0 | 0 | 0 | 0 | 165.706 | 0 | 0 | 0 | 0
2018-03 | 243.151 | 420.519 | 0 | 0 | 0.96195 | 0 | 3.3865 | 206.0543 | 0 | 0 | 0 | 0
2018-04 | 140.7769 | 504.8861 | 0 | 0 | 2.491 | 0 | 0 | 247.3942 | 0 | 0 | 0 | 0
2018-05 | 88.4353 | 520.2692 | 122.6576 | 0 | 5.3903 | 0 | 0 | 254.9319 | 0 | 0 | 13.0458 | 0
2018-06 | 285.2016 | 525.1722 | 0 | 0 | 0 | 0 | 0 | 257.3344 | 0 | 0 | 0 | 0
2018-07 | 137.6038 | 453.6213 | 0 | 0 | 0 | 0 | 9.5601 | 222.2744 | 0 | 0 | 630.151 | 0
2018-08 | 211.5255 | 519.6614 | 0 | 0 | 0 | 0 | 33.5948 | 254.6341 | 0 | 0 | 31.7572 | 0
2018-09 | 352.5964 | 476.3421 | 0 | 0 | 0 | 0 | 92.7141 | 233.4076 | 0 | 0 | 0 | 0
2018-10 | 402.548 | 392.432 | 0 | 0 | 0 | 0 | 123.5534 | 192.2917 | 0 | 0 | 0 | 0
2018-11 | 307.9596 | 322.6541 | 0 | 0 | 0 | 0 | 13.3679 | 158.1005 | 0 | 0 | 0 | 0
2018-12 | 28.1302 | 247.0204 | 0 | 0 | 0 | 0 | 2.1841 | 121.04 | 0 | 0 | 0 | 0

## Contract
period | test | basis | measured | guaranteed | guaranteed_effective | pass | shortfall_kwh | damages | bonus | excluded_share | data_share
2015 | availability | time |  | 98% |  | n/a |  |  | 0
2016 | availability | time | 95.59% | 98% |  | FAIL | 5463.716 | 327.823 | 0 | 0%
2017 | availability | time | 99.95% | 98% |  | PASS | 0 | 0 | 32.8293 | 0%
2018 | availability | time | 99.51% | 98% |  | PASS | 0 | 0 | 0.95037 | 0%
2015 | performance_ratio | pr_wc |  | 78% | 76% | n/a |  |  | 0 |  | 0%
2016 | performance_ratio | pr_wc | 66.47% | 77.61% | 75.61% | FAIL | 27781.3686 | 1666.8821 | 0 |  | 92.82%
2017 | performance_ratio | pr_wc | 69.57% | 77.22% | 75.22% | FAIL | 18628.3997 | 1117.704 | 0 |  | 99.99%
2018 | performance_ratio | pr_wc | 69.22% | 76.84% | 74.84% | FAIL | 18570.2123 | 1114.2127 | 0 |  | 99.73%
Example clauses only (configs/contract_example.yaml); check against the actual contract.

## QC
check | status | message
clock | ok | labelling offset -0.9 min
clear_days | info | 429 clear days of 945
orientation | ok | fitted tilt 6.6 deg (nominal 11.2), azimuth 175.1 deg (nominal 180)
level_clearsky | warn | level +19.0% against the clear-sky model on clear days (model uncertainty a few %)
shading | ok | no recurring low-sun shading of the sensor
sensor_soiling | ok | no decline-and-recovery pattern beyond 2.5%
drift | ok | no sustained level change beyond 2.5% against the baseline year (3 references: cs, ref, plant)
level_reference | warn | 2016: level +11.0% against poa_ref
level_reference | warn | 2017: level +11.3% against poa_ref
level_reference | warn | 2018: level +9.5% against poa_ref
level_reference | info | POA rescaled by 1/1.110
gaps | info | 1933 daylight intervals filled from the reference

## Downtime
inverter | start | end | hours | energy_kwh | category
INV1 | 2016-01-06 14:30 | 2016-01-06 14:45 | 0.25 | 4.5679 | unlogged
INV1 | 2016-02-03 10:00 | 2016-02-03 10:15 | 0.25 | 22.4449 | unlogged
INV1 | 2016-04-09 11:30 | 2016-04-09 11:45 | 0.25 | 4.6789 | unlogged
INV1 | 2016-06-04 05:45 | 2016-06-04 18:00 | 12.25 | 865.329 | unlogged
INV1 | 2016-06-05 05:15 | 2016-06-05 18:00 | 12.75 | 878.9316 | unlogged
INV1 | 2016-06-06 05:00 | 2016-06-06 18:00 | 13 | 891.2529 | unlogged
INV1 | 2016-06-07 05:15 | 2016-06-07 18:00 | 12.75 | 859.8061 | unlogged
INV1 | 2016-06-08 05:15 | 2016-06-08 18:15 | 13 | 813.8685 | unlogged
INV1 | 2016-06-09 05:15 | 2016-06-09 17:00 | 11.75 | 650.6491 | unlogged
INV1 | 2016-06-09 17:45 | 2016-06-09 18:00 | 0.25 | 1.9901 | unlogged
INV1 | 2016-06-10 05:30 | 2016-06-10 18:00 | 12.5 | 831.7462 | unlogged
INV1 | 2016-06-11 05:15 | 2016-06-11 18:00 | 12.75 | 778.236 | unlogged
INV1 | 2016-06-12 05:00 | 2016-06-12 17:00 | 12 | 808.1869 | unlogged
INV1 | 2016-06-12 17:45 | 2016-06-12 18:00 | 0.25 | 2.2396 | unlogged
INV1 | 2016-06-13 05:15 | 2016-06-13 18:00 | 12.75 | 879.9864 | unlogged
INV1 | 2016-06-14 05:15 | 2016-06-14 07:15 | 2 | 64.6283 | unlogged
INV1 | 2016-06-14 07:30 | 2016-06-14 18:00 | 10.5 | 835.3884 | unlogged
INV1 | 2016-06-15 05:15 | 2016-06-15 08:15 | 3 | 157.6216 | unlogged
INV1 | 2016-06-15 08:30 | 2016-06-15 18:00 | 9.5 | 773.1979 | unlogged
INV1 | 2016-06-16 05:15 | 2016-06-16 11:30 | 6.25 | 476.9624 | unlogged
INV1 | 2016-07-10 12:30 | 2016-07-10 12:45 | 0.25 | 25.4182 | unlogged
INV1 | 2016-10-10 09:30 | 2016-10-10 09:45 | 0.25 | 17.7346 | unlogged
INV1 | 2016-10-26 16:15 | 2016-10-26 16:30 | 0.25 | 1.6794 | unlogged
INV1 | 2016-10-28 13:00 | 2016-10-28 13:15 | 0.25 | 2.4786 | unlogged
INV1 | 2016-12-01 11:15 | 2016-12-01 11:30 | 0.25 | 18.9377 | unlogged
INV1 | 2017-03-03 17:00 | 2017-03-03 17:15 | 0.25 | 2.6366 | unlogged
INV1 | 2017-03-23 17:15 | 2017-03-23 17:30 | 0.25 | 2.8125 | unlogged
INV1 | 2017-03-24 17:00 | 2017-03-24 17:15 | 0.25 | 2.9348 | unlogged
INV1 | 2017-03-30 15:00 | 2017-03-30 15:15 | 0.25 | 6.9208 | unlogged
INV1 | 2017-04-03 12:00 | 2017-04-03 12:15 | 0.25 | 2.1715 | unlogged
INV1 | 2017-06-03 10:30 | 2017-06-03 10:45 | 0.25 | 24.6504 | unlogged
INV1 | 2017-06-25 17:00 | 2017-06-25 17:15 | 0.25 | 6.9675 | unlogged
INV1 | 2017-11-04 16:00 | 2017-11-04 16:15 | 0.25 | 2.3417 | unlogged
INV1 | 2018-03-15 17:00 | 2018-03-15 17:15 | 0.25 | 3.5266 | unlogged
INV1 | 2018-07-11 15:15 | 2018-07-11 15:30 | 0.25 | 9.676 | unlogged
INV1 | 2018-08-23 06:00 | 2018-08-23 06:15 | 0.25 | 5.979 | unlogged
INV1 | 2018-08-24 06:00 | 2018-08-24 06:15 | 0.25 | 6.0127 | unlogged
INV1 | 2018-08-27 06:00 | 2018-08-27 06:15 | 0.25 | 6.2371 | unlogged
INV1 | 2018-08-28 06:15 | 2018-08-28 06:30 | 0.25 | 6.2562 | unlogged
INV1 | 2018-08-29 18:30 | 2018-08-29 18:45 | 0.25 | 1.8548 | unlogged
INV1 | 2018-08-31 06:00 | 2018-08-31 06:30 | 0.5 | 11.4912 | unlogged
INV1 | 2018-09-04 06:00 | 2018-09-04 06:30 | 0.5 | 12.1967 | unlogged
INV1 | 2018-09-07 06:00 | 2018-09-07 06:15 | 0.25 | 5.1744 | unlogged
INV1 | 2018-09-11 06:15 | 2018-09-11 06:30 | 0.25 | 5.8616 | unlogged
INV1 | 2018-09-13 06:15 | 2018-09-13 06:30 | 0.25 | 5.5725 | unlogged
INV1 | 2018-09-17 06:15 | 2018-09-17 06:45 | 0.5 | 10.3915 | unlogged
INV1 | 2018-09-20 06:00 | 2018-09-20 06:30 | 0.5 | 9.415 | unlogged
INV1 | 2018-09-21 06:00 | 2018-09-21 06:15 | 0.25 | 5.1238 | unlogged
INV1 | 2018-09-23 06:00 | 2018-09-23 06:30 | 0.5 | 8.3425 | unlogged
INV1 | 2018-09-25 06:00 | 2018-09-25 06:45 | 0.75 | 14.3235 | unlogged
INV1 | 2018-09-26 06:00 | 2018-09-26 06:15 | 0.25 | 4.8867 | unlogged
INV1 | 2018-09-27 06:15 | 2018-09-27 06:30 | 0.25 | 4.538 | unlogged
INV1 | 2018-09-28 06:15 | 2018-09-28 06:30 | 0.25 | 4.7555 | unlogged
INV1 | 2018-09-29 06:15 | 2018-09-29 06:30 | 0.25 | 4.4302 | unlogged
INV1 | 2018-09-30 06:30 | 2018-09-30 07:00 | 0.5 | 8.5913 | unlogged
INV1 | 2018-10-02 06:15 | 2018-10-02 06:30 | 0.25 | 3.0606 | unlogged
INV1 | 2018-10-02 17:30 | 2018-10-02 17:45 | 0.25 | 2.1563 | unlogged
INV1 | 2018-10-04 06:15 | 2018-10-04 06:45 | 0.5 | 9.1349 | unlogged
INV1 | 2018-10-05 06:00 | 2018-10-05 06:15 | 0.25 | 4.2054 | unlogged
INV1 | 2018-10-06 06:30 | 2018-10-06 06:45 | 0.25 | 3.102 | unlogged
INV1 | 2018-10-09 06:00 | 2018-10-09 06:15 | 0.25 | 3.7363 | unlogged
INV1 | 2018-10-10 06:00 | 2018-10-10 06:15 | 0.25 | 4.1555 | unlogged
INV1 | 2018-10-10 06:45 | 2018-10-10 07:00 | 0.25 | 4.1555 | unlogged
INV1 | 2018-10-12 06:00 | 2018-10-12 06:15 | 0.25 | 3.6136 | unlogged
INV1 | 2018-10-12 06:45 | 2018-10-12 07:00 | 0.25 | 3.6136 | unlogged
INV1 | 2018-10-14 17:30 | 2018-10-14 17:45 | 0.25 | 1.8206 | unlogged
INV1 | 2018-10-15 06:15 | 2018-10-15 06:30 | 0.25 | 4.1999 | unlogged
INV1 | 2018-10-16 06:00 | 2018-10-16 06:15 | 0.25 | 3.3899 | unlogged
INV1 | 2018-10-17 06:00 | 2018-10-17 06:15 | 0.25 | 3.7394 | unlogged
INV1 | 2018-10-17 06:45 | 2018-10-17 07:00 | 0.25 | 3.7394 | unlogged
INV1 | 2018-10-20 06:00 | 2018-10-20 06:30 | 0.5 | 7.3093 | unlogged
INV1 | 2018-10-21 06:15 | 2018-10-21 06:30 | 0.25 | 2.0702 | unlogged
INV1 | 2018-10-22 06:45 | 2018-10-22 07:15 | 0.5 | 12.5004 | unlogged
INV1 | 2018-10-23 06:30 | 2018-10-23 07:00 | 0.5 | 6.0502 | unlogged
INV1 | 2018-10-25 06:00 | 2018-10-25 06:15 | 0.25 | 2.8067 | unlogged
INV1 | 2018-10-25 06:30 | 2018-10-25 06:45 | 0.25 | 3.1717 | unlogged
INV1 | 2018-10-26 06:00 | 2018-10-26 06:15 | 0.25 | 2.7149 | unlogged
INV1 | 2018-10-27 06:00 | 2018-10-27 07:00 | 1 | 10.3515 | unlogged
INV1 | 2018-10-28 06:00 | 2018-10-28 06:15 | 0.25 | 2.4372 | unlogged
INV1 | 2018-10-28 07:00 | 2018-10-28 07:15 | 0.25 | 8.5009 | unlogged
INV1 | 2018-10-29 06:00 | 2018-10-29 06:15 | 0.25 | 2.276 | unlogged
INV1 | 2018-10-29 06:30 | 2018-10-29 06:45 | 0.25 | 2.276 | unlogged
INV1 | 2018-10-30 06:00 | 2018-10-30 07:00 | 1 | 9.839 | unlogged
INV1 | 2018-10-31 06:00 | 2018-10-31 06:15 | 0.25 | 2.6022 | unlogged
INV1 | 2018-11-02 06:15 | 2018-11-02 06:45 | 0.5 | 4.9339 | unlogged
INV1 | 2018-11-03 06:15 | 2018-11-03 06:30 | 0.25 | 2.2706 | unlogged
INV1 | 2018-11-05 06:15 | 2018-11-05 06:30 | 0.25 | 2.2465 | unlogged
INV1 | 2018-11-28 15:30 | 2018-11-28 15:45 | 0.25 | 3.4015 | unlogged
INV1 | 2018-11-29 13:00 | 2018-11-29 13:15 | 0.25 | 2.1144 | unlogged
INV1 | 2018-12-25 07:15 | 2018-12-25 07:30 | 0.25 | 2.4276 | unlogged