## Summary
Plant | PVDAQ-1276 (building B)
DC / AC [kW] | 68.5 / 50.0
Location | 36.1952, -115.1582
Report time zone | Etc/GMT+8
Months | 2016-01 .. 2018-12
Budget P50 [kWh] | 347958.6056
Actual [kWh] | 282104.7543
Deviation [%] | -18.93%
Bridge method | sequential
Unexplained residual [kWh] | -36267.2728
YoY performance trend [%/yr] | 0.7183%
QC findings (warn/fail) | 4
Note | Working material. PR definitions follow public descriptions of IEC 61724-1 and NREL weather-corrected PR; not a certified implementation. Contract clauses are examples.

## Bridge
Month | Coverage | Budget P50 [kWh] | Actual [kWh] | Deviation [kWh] | Deviation [%] | Irradiance [kWh] | Temperature [kWh] | Degradation [kWh] | Soiling [kWh] | Snow [kWh] | Clipping [kWh] | Availability [kWh] | Curtailment [kWh] | Data gaps [kWh] | Unexplained [kWh] | Check [kWh] | POA actual [kWh/m2] | POA budget [kWh/m2] | PR | PR weather-corr. | PR budget | Availability time | Availability energy
2016-01 | 100% | 6872.9659 | 4890.775 | -1982.1909 | -28.84% | -944.8768 | -42.5 | -127.8189 | 89.4322 | 0 | 0 | 58.1593 | 0 | 0 | -1014.5866 | 0 | 104.9062 | 121.3242 | 68.08% | 63.49% | 82.72% | 100% | 100%
2016-02 | 100% | 7693.8646 | 7292.15 | -401.7146 | -5.221% | 1479.5061 | -398.2156 | -194.03 | 176.8939 | 0 | -17.2545 | 86.678 | 0 | -10.2409 | -1525.0516 | 0 | 161.4569 | 135.2342 | 65.95% | 63.45% | 83.08% | 100% | 100%
2016-03 | 100% | 10003.8241 | 8755.75 | -1248.0741 | -12.48% | 102.235 | -273.7764 | -221.41 | 198.7984 | 0 | -21.305 | 97.0795 | 0 | -3.9318 | -1125.7636 | 0 | 186.1037 | 184.0676 | 68.7% | 67.55% | 79.36% | 100% | 100%
2016-04 | 100% | 11864.5749 | 7562.95 | -4301.6249 | -36.26% | -1613.0828 | 148.5932 | -238.3436 | 160.8766 | -45.5716 | -12.7253 | 100.7013 | 0 | -1918.5161 | -883.5565 | 0 | 198.6291 | 229.5549 | 55.6% | 54.74% | 75.47% | 99.91% | 99.97%
2016-05 | 100% | 13247.9313 | 11091.4 | -2156.5313 | -16.28% | -1278.2786 | 75.4084 | -281.0189 | 245.7038 | -52.6692 | 21.6605 | 118.8287 | 0 | 0 | -1006.1661 | 0 | 236.418 | 261.4334 | 68.51% | 68.97% | 74% | 100% | 100%
2016-06 | 100% | 12989.321 | 10810.2 | -2179.121 | -16.78% | -1101.7236 | -569.2205 | -268.5708 | 228.669 | 0 | 43.1142 | 111.6142 | 0 | -7.1063 | -615.8972 | 0 | 242 | 264.1272 | 65.23% | 71.47% | 71.81% | 100% | 100%
2016-07 | 100% | 11650.7641 | 11128.125 | -522.6391 | -4.486% | 366.5622 | -448.1801 | -279.2208 | 232.7655 | 0 | 1.5467 | 102.8455 | 0 | -10.6614 | -488.2968 | 0 | 247.8465 | 239.9824 | 65.57% | 72.2% | 70.89% | 99.94% | 99.9%
2016-08 | 100% | 11242.9076 | 10016.85 | -1226.0576 | -10.91% | -350.4274 | -215.0889 | -262.2038 | 214.7019 | 0 | -10.3179 | 105.2039 | 0 | 0 | -707.9255 | 0 | 222.8099 | 229.6603 | 65.65% | 70.63% | 71.49% | 100% | 100%
2016-09 | 100% | 9831.5238 | 9129.325 | -702.1988 | -7.142% | 362.8072 | 46.9454 | -255.6293 | 202.6016 | 0 | -8.434 | 100.8651 | 0 | 0 | -1151.3547 | 0 | 203.078 | 195.563 | 65.65% | 67.51% | 73.41% | 100% | 100%
2016-10 | 100% | 8154.7135 | 7147.45 | -1007.2635 | -12.35% | 176.1098 | 102.2299 | -213.8099 | 106.1442 | 0 | -17.3589 | 75.3939 | 0 | 0 | -1235.9724 | 0 | 157.3637 | 153.7877 | 66.33% | 64.56% | 77.43% | 99.84% | 99.89%
2016-11 | 100% | 6771.69 | 5788.35 | -983.34 | -14.52% | 524.8269 | -126.1437 | -184.8111 | 16.4689 | 0 | -0.34301 | 70.5612 | 0 | 0 | -1283.8992 | 0 | 131.1953 | 121.565 | 64.43% | 61.63% | 81.34% | 100% | 100%
2016-12 | 100% | 5662.7554 | 4308.3 | -1354.4554 | -23.92% | -156.9307 | 97.867 | -146.6698 | 6.0971 | 0 | 0 | 52.397 | 0 | 0 | -1207.2161 | 0 | 95.7963 | 98.2822 | 65.67% | 58.94% | 84.14% | 99.89% | 99.94%
2017-01 | 100% | 6872.9659 | 5036.025 | -1836.9409 | -26.73% | -790.0718 | -17.2945 | -161.4982 | 50.6928 | 0 | 0 | 59.6374 | 0 | -3.8209 | -974.5856 | 0 | 107.6305 | 121.3242 | 68.33% | 63.47% | 82.72% | 100% | 100%
2017-02 | 100% | 7693.8646 | 5509.975 | -2183.8896 | -28.38% | -1237.0513 | -69.2084 | -172.503 | -192.387 | 0 | -0.28134 | 62.7788 | 0 | 0 | -575.2373 | 0 | 113.8473 | 135.2342 | 70.67% | 65.94% | 83.08% | 100% | 100%
2017-03 | 100% | 10003.8241 | 8959.525 | -1044.2991 | -10.44% | 394.2674 | 61.9228 | -286.5118 | 210.4362 | 0 | -101.0541 | 101.3355 | 0 | -18.6122 | -1406.0829 | 0 | 191.4501 | 184.0676 | 68.34% | 65.19% | 79.36% | 99.92% | 99.98%
2017-04 | 100% | 11864.5749 | 10434.025 | -1430.5499 | -12.06% | -466.2088 | 146.5617 | -321.0112 | 233.8578 | 0 | -48.0546 | 112.4631 | 0 | 0 | -1088.1579 | 0 | 220.7757 | 229.5549 | 69.01% | 68.04% | 75.47% | 99.93% | 99.99%
2017-05 | 100% | 13247.9313 | 11252.3 | -1995.6313 | -15.06% | -876.1398 | -163.1949 | -344.3426 | 247.7969 | 0 | 98.4161 | 119.8409 | 0 | 0 | -1078.0079 | 0 | 244.3064 | 261.4334 | 67.26% | 68.92% | 74% | 100% | 100%
2017-06 | 100% | 12989.321 | 11094.4 | -1894.921 | -14.59% | -613.6743 | -532.0517 | -338.8585 | 238.0835 | 0 | 38.1925 | 98.2258 | 0 | -17.8463 | -766.992 | 0 | 251.8538 | 264.1272 | 64.33% | 70.16% | 71.81% | 99.87% | 99.84%
2017-07 | 100% | 11650.7641 | 9865.175 | -1785.5891 | -15.33% | -954.9744 | -367.4954 | -299.6496 | 198.7077 | 0 | 1.3739 | 101.2994 | 0 | 0 | -464.8508 | 0 | 220.6198 | 239.9824 | 65.3% | 71.68% | 70.89% | 100% | 100%
2017-08 | 100% | 11242.9076 | 7437.85 | -3805.0576 | -33.84% | -595.1854 | -236.9541 | -306.3819 | 193.6535 | 0 | 0 | 102.0645 | 0 | -2476.3039 | -485.9503 | 0 | 217.832 | 229.6603 | 49.86% | 53.76% | 71.49% | 100% | 100%
2017-09 | 100% | 9831.5238 | 1766.15 | -8065.3738 | -82.04% | -302.4435 | 144.3761 | -288.7106 | 193.46 | 0 | -34.3169 | 90.5386 | 0 | -6689.065 | -1179.2124 | 0 | 189.8563 | 195.563 | 13.58% | 13.84% | 73.41% | 99.6% | 99.76%
2017-10 | 100% | 8154.7135 | 8117.425 | -37.2885 | -0.4573% | 1547.0198 | 33.9523 | -294.3445 | 169.8449 | 0 | -42.8389 | 95.3671 | 0 | 0 | -1546.2891 | 0 | 183.1424 | 153.7877 | 64.72% | 63.5% | 77.43% | 100% | 100%
2017-11 | 100% | 6771.69 | 5535.5 | -1236.19 | -18.26% | 168.9716 | 82.3463 | -215.2087 | 43.376 | 0 | -1.7725 | 67.8953 | 0 | -2.7675 | -1379.0305 | 0 | 124.8376 | 121.565 | 64.75% | 60.32% | 81.34% | 99.9% | 99.98%
2017-12 | 100% | 5662.7554 | 4996.325 | -666.4304 | -11.77% | 1057.7467 | 41.3979 | -209.9344 | -30.6508 | 0 | 0 | 66.1815 | 0 | 0 | -1591.1712 | 1.1369e-13 | 116.6821 | 98.2822 | 62.53% | 56.7% | 84.14% | 100% | 100%
2018-01 | 100% | 6872.9659 | 5200.075 | -1672.8909 | -24.34% | -348.3495 | -193.1333 | -199.3782 | 54.7728 | 0 | -0.20166 | 61.9405 | 0 | 0 | -1048.5415 | 0 | 115.3592 | 121.3242 | 65.83% | 62.66% | 82.72% | 100% | 100%
2018-02 | 100% | 7693.8646 | 6522.625 | -1171.2396 | -15.22% | 252.1327 | -292.1909 | -243.8791 | -0.82443 | 0 | -2.2442 | 74.8478 | 0 | 0 | -959.0814 | 0 | 139.8983 | 135.2342 | 68.08% | 65.08% | 83.08% | 100% | 100%
2018-03 | 100% | 10003.8241 | 8578.35 | -1425.4741 | -14.25% | -352.3137 | -159.2217 | -306.2202 | 88.5223 | 0 | 4.5804 | 92.7886 | 0 | 0 | -793.6098 | 0 | 177.7996 | 184.0676 | 70.45% | 68.6% | 79.36% | 100% | 100%
2018-04 | 100% | 11864.5749 | 10349.75 | -1514.8249 | -12.77% | -540.7618 | -1.957 | -369.7878 | 228.1937 | 0 | 36.3724 | 110.627 | 0 | 0 | -977.5113 | 0 | 219.318 | 229.5549 | 68.91% | 68.74% | 75.47% | 100% | 100%
2018-05 | 100% | 13247.9313 | 10909.925 | -2338.0063 | -17.65% | -1374.176 | -222.4442 | -385.251 | 203.3532 | 0 | 98.5117 | 113.7986 | 0 | -5.7155 | -766.083 | 0 | 234.5097 | 261.4334 | 67.94% | 69.95% | 74% | 100% | 100%
2018-06 | 100% | 12989.321 | 11326.55 | -1662.771 | -12.8% | -583.5589 | -522.0961 | -397.7056 | 129.2193 | 0 | 45.0741 | 116.0198 | 0 | 0 | -449.7237 | 0 | 252.4653 | 264.1272 | 65.51% | 71.39% | 71.81% | 100% | 100%
2018-07 | 100% | 11650.7641 | 9573.45 | -2077.3141 | -17.83% | -754.3749 | -284.7133 | -359.4073 | 170.9427 | 0 | 1.4046 | 78.2383 | 0 | -244.1536 | -685.2505 | 0 | 224.6102 | 239.9824 | 62.24% | 67.82% | 70.89% | 99.42% | 99.74%
2018-08 | 100% | 11242.9076 | 10012.5542 | -1230.3534 | -10.94% | -393.4566 | 961.8339 | -404.941 | 235.1339 | 0 | -76.9754 | 96.8059 | 0 | -17.956 | -1630.798 | 0 | 221.8244 | 229.6603 | 65.91% | 64.54% | 71.49% | 99.06% | 99.82%
2018-09 | 100% | 9831.5238 | 9121.825 | -709.6988 | -7.219% | 296.3616 | 689.8122 | -375.1678 | 215.2655 | 0 | -53.4949 | 66.2166 | 0 | 0 | -1548.692 | 0 | 201.6655 | 195.563 | 66.05% | 64.26% | 73.41% | 98.49% | 99.57%
2018-10 | 100% | 8154.7135 | 7639.825 | -514.8885 | -6.314% | 450.5803 | 303.4121 | -312.63 | 177.2021 | 0 | -13.5055 | 37.4132 | 0 | 0 | -1157.3607 | -1.1369e-13 | 162.4346 | 153.7877 | 68.68% | 65.51% | 77.43% | 96.99% | 99.36%
2018-11 | 100% | 6771.69 | 4943.525 | -1828.165 | -27% | 523.4907 | 30.7288 | -259.8993 | 145.6609 | 0 | -0.85963 | -831.8572 | 0 | -10.6507 | -1424.7785 | 0 | 131.1126 | 121.565 | 55.06% | 51.65% | 81.34% | 81.07% | 84.55%
2018-12 | 99.97% | 5660.8526 | 0 | -5660.8526 | -100% | 103.6086 | -146.5618 | -201.665 | 111.6519 | 0 | 0 | -5483.2981 | 0 | 0 | -44.5882 | 0 | 100.1604 | 98.2491 | 0% | 0% | 84.14% | 0% | 0.7878%

## Losses
Month | Soiling measured [kWh] | Soiling budget [kWh] | Snow measured [kWh] | Snow budget [kWh] | Clipping measured [kWh] | Clipping budget [kWh] | Availability measured [kWh] | Availability budget [kWh] | Curtailment measured [kWh] | Curtailment budget [kWh] | Data gaps measured [kWh] | Data gaps budget [kWh]
2016-01 | 29.2603 | 118.6924 | 0 | 0 | 0 | 0 | 0 | 58.1593 | 0 | 0 | 0 | 0
2016-02 | 0 | 176.8939 | 0 | 0 | 17.2545 | 0 | 0 | 86.678 | 0 | 0 | 10.2409 | 0
2016-03 | 0 | 198.7984 | 0 | 0 | 54.4735 | 33.1685 | 0 | 97.0795 | 0 | 0 | 3.9318 | 0
2016-04 | 50.8501 | 211.7267 | 45.5716 | 0 | 122.9488 | 110.2235 | 1.9426 | 102.6439 | 0 | 0 | 1918.5161 | 0
2016-05 | 0 | 245.7038 | 52.6692 | 0 | 134.9571 | 156.6176 | 0 | 118.8287 | 0 | 0 | 0 | 0
2016-06 | 0 | 228.669 | 0 | 0 | 0.2483 | 43.3625 | 0 | 111.6142 | 0 | 0 | 7.1063 | 0
2016-07 | 0 | 232.7655 | 0 | 0 | 0 | 1.5467 | 11.1941 | 114.0397 | 0 | 0 | 10.6614 | 0
2016-08 | 0 | 214.7019 | 0 | 0 | 10.3179 | 0 | 0 | 105.2039 | 0 | 0 | 0 | 0
2016-09 | 3.2456 | 205.8472 | 0 | 0 | 8.434 | 0 | 0 | 100.8651 | 0 | 0 | 0 | 0
2016-10 | 63.2898 | 169.434 | 0 | 0 | 17.3589 | 0 | 7.6288 | 83.0227 | 0 | 0 | 0 | 0
2016-11 | 127.5336 | 144.0025 | 0 | 0 | 0.34301 | 0 | 0 | 70.5612 | 0 | 0 | 0 | 0
2016-12 | 106.3956 | 112.4927 | 0 | 0 | 0 | 0 | 2.7244 | 55.1214 | 0 | 0 | 0 | 0
2017-01 | 71.0162 | 121.709 | 0 | 0 | 0 | 0 | 0 | 59.6374 | 0 | 0 | 3.8209 | 0
2017-02 | 320.507 | 128.12 | 0 | 0 | 0.28134 | 0 | 0 | 62.7788 | 0 | 0 | 0 | 0
2017-03 | 0 | 210.4362 | 0 | 0 | 136.1644 | 35.1102 | 1.4271 | 102.7627 | 0 | 0 | 18.6122 | 0
2017-04 | 0 | 233.8578 | 0 | 0 | 169.7994 | 121.7448 | 0.90978 | 113.3729 | 0 | 0 | 0 | 0
2017-05 | 0 | 247.7969 | 0 | 0 | 59.5356 | 157.9517 | 0 | 119.8409 | 0 | 0 | 0 | 0
2017-06 | 0 | 238.0835 | 0 | 0 | 6.9554 | 45.1478 | 17.9837 | 116.2095 | 0 | 0 | 17.8463 | 0
2017-07 | 8.0539 | 206.7616 | 0 | 0 | 0 | 1.3739 | 0 | 101.2994 | 0 | 0 | 0 | 0
2017-08 | 14.6414 | 208.2949 | 0 | 0 | 0 | 0 | 0 | 102.0645 | 0 | 0 | 2476.3039 | 0
2017-09 | 0 | 193.46 | 0 | 0 | 34.3169 | 0 | 4.2568 | 94.7954 | 0 | 0 | 6689.065 | 0
2017-10 | 24.7818 | 194.6267 | 0 | 0 | 42.8389 | 0 | 0 | 95.3671 | 0 | 0 | 0 | 0
2017-11 | 96.962 | 140.3381 | 0 | 0 | 1.7725 | 0 | 0.87038 | 68.7656 | 0 | 0 | 2.7675 | 0
2017-12 | 165.7151 | 135.0642 | 0 | 0 | 0 | 0 | 0 | 66.1815 | 0 | 0 | 0 | 0
2018-01 | 71.6362 | 126.4091 | 0 | 0 | 0.20166 | 0 | 0 | 61.9405 | 0 | 0 | 0 | 0
2018-02 | 153.5749 | 152.7505 | 0 | 0 | 2.2442 | 0 | 0 | 74.8478 | 0 | 0 | 0 | 0
2018-03 | 101.4891 | 190.0114 | 0 | 0 | 27.122 | 31.7025 | 0 | 92.7886 | 0 | 0 | 0 | 0
2018-04 | 0 | 228.1937 | 0 | 0 | 82.4238 | 118.7961 | 0 | 110.627 | 0 | 0 | 0 | 0
2018-05 | 31.9498 | 235.303 | 0 | 0 | 51.4761 | 149.9878 | 0 | 113.7986 | 0 | 0 | 5.7155 | 0
2018-06 | 108.4756 | 237.695 | 0 | 0 | 0 | 45.0741 | 0 | 116.0198 | 0 | 0 | 0 | 0
2018-07 | 40.4294 | 211.3721 | 0 | 0 | 0 | 1.4046 | 25.32 | 103.5583 | 0 | 0 | 244.1536 | 0
2018-08 | 0 | 235.1339 | 0 | 0 | 76.9754 | 0 | 18.4097 | 115.2156 | 0 | 0 | 17.956 | 0
2018-09 | 0 | 215.2655 | 0 | 0 | 53.4949 | 0 | 39.2635 | 105.4801 | 0 | 0 | 0 | 0
2018-10 | 0 | 177.2021 | 0 | 0 | 13.5055 | 0 | 49.4159 | 86.829 | 0 | 0 | 0 | 0
2018-11 | 0 | 145.6609 | 0 | 0 | 0.85963 | 0 | 903.2311 | 71.3738 | 0 | 0 | 10.6507 | 0
2018-12 | 0 | 111.6519 | 0 | 0 | 0 | 0 | 5538.0075 | 54.7094 | 0 | 0 | 0 | 0

## Contract
period | test | basis | measured | guaranteed | guaranteed_effective | pass | shortfall_kwh | damages | bonus | excluded_share | data_share
2015 | availability | time |  | 98% |  | n/a |  |  | 0 | 100%
2016 | availability | time | 99.97% | 98% |  | PASS | 0 | 0 | 15.3324 | 0%
2017 | availability | time | 99.96% | 98% |  | PASS | 0 | 0 | 13.8408 | 0%
2018 | availability | time | 91.82% | 98% |  | FAIL | 6898.8793 | 413.9328 | 0 | 0%
2015 | performance_ratio | pr_wc |  | 78% | 76% | n/a |  |  | 0 |  | 0%
2016 | performance_ratio | pr_wc | 67.48% | 77.61% | 75.61% | FAIL | 11731.7 | 703.902 | 0 |  | 98.12%
2017 | performance_ratio | pr_wc | 66.73% | 77.22% | 75.22% | FAIL | 11397.5951 | 683.8557 | 0 |  | 90.75%
2018 | performance_ratio | pr_wc | 63.11% | 76.84% | 74.84% | FAIL | 17408.709 | 1044.5225 | 0 |  | 99.74%
Example clauses only (configs/contract_example.yaml); check against the actual contract.

## QC
check | status | message
clock | ok | labelling offset -0.9 min
clear_days | info | 421 clear days of 923
orientation | ok | fitted tilt 6.9 deg (nominal 5), azimuth 175.0 deg (nominal 180)
level_clearsky | warn | level +22.9% against the clear-sky model on clear days (model uncertainty a few %)
shading | ok | no recurring low-sun shading of the sensor
sensor_soiling | ok | no decline-and-recovery pattern beyond 2.5%
drift | ok | no sustained level change beyond 2.5% against the baseline year (3 references: cs, ref, plant)
level_reference | warn | 2016: level +16.0% against poa_ref
level_reference | warn | 2017: level +16.3% against poa_ref
level_reference | warn | 2018: level +14.2% against poa_ref
level_reference | info | POA rescaled by 1/1.160
gaps | info | 3036 daylight intervals filled from the reference

## Downtime
inverter | start | end | hours | energy_kwh | category
INV1 | 2016-04-09 11:30 | 2016-04-09 11:45 | 0.25 | 2.1194 | unlogged
INV1 | 2016-07-10 12:30 | 2016-07-10 12:45 | 0.25 | 11.6843 | unlogged
INV1 | 2016-10-10 09:30 | 2016-10-10 09:45 | 0.25 | 8.1509 | unlogged
INV1 | 2016-10-26 16:15 | 2016-10-26 16:30 | 0.25 | 0.78112 | unlogged
INV1 | 2016-12-11 08:30 | 2016-12-11 08:45 | 0.25 | 3.4688 | unlogged
INV1 | 2017-03-05 16:30 | 2017-03-05 16:45 | 0.25 | 1.6473 | unlogged
INV1 | 2017-04-03 12:00 | 2017-04-03 12:15 | 0.25 | 1.0031 | unlogged
INV1 | 2017-06-03 10:30 | 2017-06-03 10:45 | 0.25 | 11.4263 | unlogged
INV1 | 2017-06-26 15:15 | 2017-06-26 15:30 | 0.25 | 7.7952 | unlogged
INV1 | 2017-09-25 07:00 | 2017-09-25 07:15 | 0.25 | 4.8478 | unlogged
INV1 | 2017-11-04 16:00 | 2017-11-04 16:15 | 0.25 | 1.0833 | unlogged
INV1 | 2018-07-11 15:15 | 2018-07-11 17:30 | 2.25 | 27.0742 | unlogged
INV1 | 2018-08-05 05:15 | 2018-08-05 05:30 | 0.25 | 0.87734 | unlogged
INV1 | 2018-08-06 05:00 | 2018-08-06 05:30 | 0.5 | 1.6484 | unlogged
INV1 | 2018-08-06 05:45 | 2018-08-06 06:00 | 0.25 | 0.82449 | unlogged
INV1 | 2018-08-07 05:15 | 2018-08-07 05:30 | 0.25 | 0.79371 | unlogged
INV1 | 2018-08-07 05:45 | 2018-08-07 06:00 | 0.25 | 0.79427 | unlogged
INV1 | 2018-08-09 05:00 | 2018-08-09 05:45 | 0.75 | 2.1838 | unlogged
INV1 | 2018-08-23 06:00 | 2018-08-23 06:15 | 0.25 | 2.8875 | unlogged
INV1 | 2018-08-24 06:00 | 2018-08-24 06:15 | 0.25 | 2.8835 | unlogged
INV1 | 2018-08-27 06:00 | 2018-08-27 06:15 | 0.25 | 2.9872 | unlogged
INV1 | 2018-08-31 06:00 | 2018-08-31 06:30 | 0.5 | 5.4954 | unlogged
INV1 | 2018-09-04 06:00 | 2018-09-04 06:30 | 0.5 | 5.767 | unlogged
INV1 | 2018-09-07 06:00 | 2018-09-07 06:15 | 0.25 | 2.4578 | unlogged
INV1 | 2018-09-11 06:15 | 2018-09-11 06:30 | 0.25 | 2.7671 | unlogged
INV1 | 2018-09-13 06:15 | 2018-09-13 06:30 | 0.25 | 2.6225 | unlogged
INV1 | 2018-09-17 06:15 | 2018-09-17 06:30 | 0.25 | 2.4353 | unlogged
INV1 | 2018-09-20 06:00 | 2018-09-20 06:30 | 0.5 | 4.4039 | unlogged
INV1 | 2018-09-21 06:00 | 2018-09-21 06:15 | 0.25 | 2.3861 | unlogged
INV1 | 2018-09-23 06:00 | 2018-09-23 06:30 | 0.5 | 3.8823 | unlogged
INV1 | 2018-09-25 06:00 | 2018-09-25 06:45 | 0.75 | 6.6303 | unlogged
INV1 | 2018-09-26 06:00 | 2018-09-26 06:15 | 0.25 | 2.2572 | unlogged
INV1 | 2018-09-27 06:15 | 2018-09-27 06:30 | 0.25 | 2.0929 | unlogged
INV1 | 2018-09-28 06:15 | 2018-09-28 06:30 | 0.25 | 2.1875 | unlogged
INV1 | 2018-09-29 06:15 | 2018-09-29 06:30 | 0.25 | 2.0369 | unlogged
INV1 | 2018-09-30 06:30 | 2018-09-30 07:00 | 0.5 | 3.9396 | unlogged
INV1 | 2018-10-02 06:15 | 2018-10-02 06:30 | 0.25 | 1.4056 | unlogged
INV1 | 2018-10-04 06:15 | 2018-10-04 06:45 | 0.5 | 4.149 | unlogged
INV1 | 2018-10-05 06:00 | 2018-10-05 06:15 | 0.25 | 1.9115 | unlogged
INV1 | 2018-10-06 06:30 | 2018-10-06 06:45 | 0.25 | 1.4008 | unlogged
INV1 | 2018-10-09 06:00 | 2018-10-09 06:15 | 0.25 | 1.6874 | unlogged
INV1 | 2018-10-10 06:00 | 2018-10-10 06:15 | 0.25 | 1.8582 | unlogged
INV1 | 2018-10-10 06:45 | 2018-10-10 07:00 | 0.25 | 1.8581 | unlogged
INV1 | 2018-10-12 06:00 | 2018-10-12 06:15 | 0.25 | 1.6185 | unlogged
INV1 | 2018-10-12 06:45 | 2018-10-12 07:00 | 0.25 | 1.6185 | unlogged
INV1 | 2018-10-14 17:30 | 2018-10-14 17:45 | 0.25 | 0.8547 | unlogged
INV1 | 2018-10-15 06:15 | 2018-10-15 06:30 | 0.25 | 1.8471 | unlogged
INV1 | 2018-10-16 06:00 | 2018-10-16 06:15 | 0.25 | 1.4662 | unlogged
INV1 | 2018-10-17 06:00 | 2018-10-17 06:15 | 0.25 | 1.6366 | unlogged
INV1 | 2018-10-17 06:45 | 2018-10-17 07:00 | 0.25 | 1.6366 | unlogged
INV1 | 2018-10-20 06:00 | 2018-10-20 06:30 | 0.5 | 3.135 | unlogged
INV1 | 2018-10-21 06:15 | 2018-10-21 06:30 | 0.25 | 0.94966 | unlogged
INV1 | 2018-10-22 06:45 | 2018-10-22 07:15 | 0.5 | 5.617 | unlogged
INV1 | 2018-10-23 06:30 | 2018-10-23 07:00 | 0.5 | 2.6051 | unlogged
INV1 | 2018-10-25 06:00 | 2018-10-25 06:15 | 0.25 | 1.1803 | unlogged
INV1 | 2018-10-25 06:30 | 2018-10-25 06:45 | 0.25 | 1.3323 | unlogged
INV1 | 2018-10-26 06:00 | 2018-10-26 06:15 | 0.25 | 1.1136 | unlogged
INV1 | 2018-10-27 06:00 | 2018-10-27 07:00 | 1 | 4.2582 | unlogged
INV1 | 2018-10-28 06:00 | 2018-10-28 06:15 | 0.25 | 0.99034 | unlogged
INV1 | 2018-10-28 07:00 | 2018-10-28 07:15 | 0.25 | 3.844 | unlogged
INV1 | 2018-10-29 06:00 | 2018-10-29 06:15 | 0.25 | 0.9557 | unlogged
INV1 | 2018-10-29 06:30 | 2018-10-29 06:45 | 0.25 | 0.9557 | unlogged
INV1 | 2018-10-30 06:00 | 2018-10-30 07:00 | 1 | 3.9217 | unlogged
INV1 | 2018-10-31 06:00 | 2018-10-31 06:15 | 0.25 | 1.0354 | unlogged
INV1 | 2018-11-02 06:15 | 2018-11-02 06:45 | 0.5 | 1.8841 | unlogged
INV1 | 2018-11-03 06:15 | 2018-11-03 06:30 | 0.25 | 0.85989 | unlogged
INV1 | 2018-11-24 12:45 | 2018-11-24 15:45 | 3 | 66.356 | unlogged
INV1 | 2018-11-25 07:30 | 2018-11-25 15:45 | 8.25 | 198.0569 | unlogged
INV1 | 2018-11-26 07:15 | 2018-11-26 07:30 | 0.25 | 2.8227 | unlogged
INV1 | 2018-11-26 07:45 | 2018-11-26 15:45 | 8 | 231.0914 | unlogged
INV1 | 2018-11-27 07:00 | 2018-11-27 07:30 | 0.5 | 4.4392 | unlogged
INV1 | 2018-11-27 07:45 | 2018-11-27 13:15 | 5.5 | 148.9828 | unlogged
INV1 | 2018-11-27 13:45 | 2018-11-27 15:45 | 2 | 21.2759 | unlogged
INV1 | 2018-11-28 07:00 | 2018-11-28 07:15 | 0.25 | 2.2334 | unlogged
INV1 | 2018-11-28 07:45 | 2018-11-28 09:00 | 1.25 | 23.9186 | unlogged
INV1 | 2018-11-28 09:15 | 2018-11-28 09:45 | 0.5 | 16.1984 | unlogged
INV1 | 2018-11-28 10:00 | 2018-11-28 10:15 | 0.25 | 5.8437 | unlogged
INV1 | 2018-11-28 10:45 | 2018-11-28 14:30 | 3.75 | 106.8705 | unlogged
INV1 | 2018-11-28 15:30 | 2018-11-28 15:45 | 0.25 | 1.5302 | unlogged
INV1 | 2018-11-29 07:00 | 2018-11-29 07:15 | 0.25 | 1.5651 | unlogged
INV1 | 2018-11-29 07:30 | 2018-11-29 12:30 | 5 | 63.417 | unlogged
INV1 | 2018-11-29 12:45 | 2018-11-29 14:00 | 1.25 | 5.5361 | unlogged
INV1 | 2018-11-29 14:15 | 2018-11-29 15:30 | 1.25 | 16.0432 | unlogged
INV1 | 2018-11-30 07:15 | 2018-11-30 07:30 | 0.25 | 2.3973 | unlogged
INV1 | 2018-11-30 07:45 | 2018-11-30 15:15 | 7.5 | 200.1934 | unlogged
INV1 | 2018-11-30 15:30 | 2018-11-30 15:45 | 0.25 | 1.3916 | unlogged
INV1 | 2018-12-01 07:45 | 2018-12-01 15:45 | 8 | 223.1697 | unlogged
INV1 | 2018-12-02 07:45 | 2018-12-02 16:00 | 8.25 | 246.1808 | unlogged
INV1 | 2018-12-03 07:45 | 2018-12-03 15:45 | 8 | 237.7643 | unlogged
INV1 | 2018-12-04 07:00 | 2018-12-04 07:15 | 0.25 | 1.3762 | unlogged
INV1 | 2018-12-04 07:30 | 2018-12-04 15:45 | 8.25 | 171.846 | unlogged
INV1 | 2018-12-05 08:00 | 2018-12-05 14:45 | 6.75 | 54.9541 | unlogged
INV1 | 2018-12-06 08:00 | 2018-12-06 14:15 | 6.25 | 49.7605 | unlogged
INV1 | 2018-12-06 14:30 | 2018-12-06 15:00 | 0.5 | 3.3232 | unlogged
INV1 | 2018-12-07 07:30 | 2018-12-07 15:30 | 8 | 102.9553 | unlogged
INV1 | 2018-12-08 07:45 | 2018-12-08 16:00 | 8.25 | 214.0147 | unlogged
INV1 | 2018-12-09 07:00 | 2018-12-09 07:30 | 0.5 | 4.5699 | unlogged
INV1 | 2018-12-09 07:45 | 2018-12-09 15:45 | 8 | 219.428 | unlogged
INV1 | 2018-12-10 07:45 | 2018-12-10 15:30 | 7.75 | 173.0593 | unlogged
INV1 | 2018-12-11 07:00 | 2018-12-11 07:15 | 0.25 | 0.8952 | unlogged
INV1 | 2018-12-11 08:00 | 2018-12-11 16:00 | 8 | 217.8987 | unlogged
INV1 | 2018-12-12 07:00 | 2018-12-12 07:15 | 0.25 | 2.0226 | unlogged
INV1 | 2018-12-12 07:30 | 2018-12-12 07:45 | 0.25 | 2.0226 | unlogged
INV1 | 2018-12-12 08:00 | 2018-12-12 15:45 | 7.75 | 207.0669 | unlogged
INV1 | 2018-12-13 07:30 | 2018-12-13 15:45 | 8.25 | 222.141 | unlogged
INV1 | 2018-12-14 07:45 | 2018-12-14 15:15 | 7.5 | 117.564 | unlogged
INV1 | 2018-12-15 07:45 | 2018-12-15 15:45 | 8 | 223.662 | unlogged
INV1 | 2018-12-16 07:15 | 2018-12-16 07:45 | 0.5 | 4.0397 | unlogged
INV1 | 2018-12-16 08:00 | 2018-12-16 15:45 | 7.75 | 213.0829 | unlogged
INV1 | 2018-12-17 07:45 | 2018-12-17 15:45 | 8 | 106.3759 | unlogged
INV1 | 2018-12-18 07:00 | 2018-12-18 07:15 | 0.25 | 1.548 | unlogged
INV1 | 2018-12-18 07:30 | 2018-12-18 16:00 | 8.5 | 187.7979 | unlogged
INV1 | 2018-12-19 07:30 | 2018-12-19 07:45 | 0.25 | 1.9037 | unlogged
INV1 | 2018-12-19 08:00 | 2018-12-19 16:00 | 8 | 211.9931 | unlogged
INV1 | 2018-12-20 07:00 | 2018-12-20 07:15 | 0.25 | 1.5595 | unlogged
INV1 | 2018-12-20 07:30 | 2018-12-20 16:00 | 8.5 | 168.7977 | unlogged
INV1 | 2018-12-21 07:45 | 2018-12-21 15:45 | 8 | 128.1903 | unlogged
INV1 | 2018-12-22 08:00 | 2018-12-22 15:45 | 7.75 | 209.3691 | unlogged
INV1 | 2018-12-23 07:30 | 2018-12-23 15:45 | 8.25 | 156.2076 | unlogged
INV1 | 2018-12-24 07:30 | 2018-12-24 16:00 | 8.5 | 171.3122 | unlogged
INV1 | 2018-12-25 07:15 | 2018-12-25 07:30 | 0.25 | 1.0268 | unlogged
INV1 | 2018-12-25 08:30 | 2018-12-25 08:45 | 0.25 | 3.6269 | unlogged
INV1 | 2018-12-25 09:00 | 2018-12-25 15:45 | 6.75 | 153.3058 | unlogged
INV1 | 2018-12-26 07:30 | 2018-12-26 07:45 | 0.25 | 1.7381 | unlogged
INV1 | 2018-12-26 08:00 | 2018-12-26 15:45 | 7.75 | 216.8102 | unlogged
INV1 | 2018-12-27 07:00 | 2018-12-27 07:15 | 0.25 | 1.3678 | unlogged
INV1 | 2018-12-27 08:00 | 2018-12-27 15:30 | 7.5 | 193.3831 | unlogged
INV1 | 2018-12-28 07:30 | 2018-12-28 16:00 | 8.5 | 153.4972 | unlogged
INV1 | 2018-12-29 08:00 | 2018-12-29 15:45 | 7.75 | 225.8605 | unlogged
INV1 | 2018-12-30 08:00 | 2018-12-30 16:00 | 8 | 215.9251 | unlogged
INV1 | 2018-12-31 08:00 | 2018-12-31 15:00 | 7 | 111.5209 | unlogged
INV1 | 2018-12-31 15:15 | 2018-12-31 15:30 | 0.25 | 1.0633 | unlogged
INV1 | 2018-12-31 15:45 | 2018-12-31 16:00 | 0.25 | 1.0293 | unlogged