## Summary
Plant | PL-DEMO
DC / AC [kW] | 1320.0 / 1000.0
Location | 51.9000, 19.5000
Report time zone | Europe/Warsaw
Months | 2021-01 .. 2024-12
Budget P50 [kWh] | 5737293.7985
Actual [kWh] | 5688341.1345
Deviation [%] | -0.8532%
Bridge method | sequential
Unexplained residual [kWh] | -132048.3096
YoY performance trend [%/yr] | -0.07518%
QC findings (warn/fail) | 0
Note | Working material. PR definitions follow public descriptions of IEC 61724-1 and NREL weather-corrected PR; not a certified implementation. Contract clauses are examples.

## Bridge
Month | Coverage | Budget P50 [kWh] | Actual [kWh] | Deviation [kWh] | Deviation [%] | Irradiance [kWh] | Temperature [kWh] | Degradation [kWh] | Soiling [kWh] | Snow [kWh] | Clipping [kWh] | Availability [kWh] | Curtailment [kWh] | Data gaps [kWh] | Unexplained [kWh] | Check [kWh] | POA actual [kWh/m2] | POA budget [kWh/m2] | PR | PR weather-corr. | PR budget | Availability time | Availability energy
2021-01 | 100% | 65982.2814 | 24949.4145 | -41032.8668 | -62.19% | -24434.1632 | -665.1058 | -129.7259 | -72.1847 | -15371.5321 | 0 | 236.1237 | 0 | 0 | -596.2788 | 0 | 35.7516 | 56.1945 | 52.87% | 48.82% | 88.95% | 99.25% | 99.3%
2021-02 | 100% | 78950.2752 | 56808.9819 | -22141.2933 | -28.04% | 594.8677 | 1530.0355 | -289.4859 | 907.774 | -22917.3732 | 0 | 816.0171 | 0 | -184.1478 | -2598.9807 | 0 | 70.9374 | 70.4871 | 60.67% | 57.29% | 84.85% | 100% | 100%
2021-03 | 99.87% | 108523.8933 | 124794.4013 | 16270.508 | 14.99% | 18823.432 | -1557.6692 | -498.065 | -737.9895 | 1027.7994 | 178.4151 | 232.5625 | 0 | 0 | -1197.9773 | 0 | 109.9759 | 93.9295 | 85.97% | 82.76% | 87.53% | 99.48% | 99.18%
2021-04 | 100% | 160467.8408 | 163290.6114 | 2822.7706 | 1.759% | 7968.3958 | 2682.9435 | -748.67 | 1309.5336 | 0 | 286.5912 | -1078.0829 | -4985.2837 | 0 | -2612.6568 | 0 | 152.2387 | 145.1624 | 81.26% | 80.06% | 83.75% | 98.59% | 98.31%
2021-05 | 100% | 125981.4234 | 186806.1757 | 60824.7522 | 48.28% | 67964.1936 | -1402.1848 | -922.9086 | 2404.8594 | 0 | 739.5177 | -593.97 | -3868.404 | -491.1759 | -3005.1752 | 0 | 175.6191 | 114.7012 | 80.58% | 81.17% | 83.21% | 99.19% | 98.66%
2021-06 | 100% | 195997.3563 | 202557.5136 | 6560.1573 | 3.347% | 14784.648 | -2016.9406 | -1085.7196 | 1622.1591 | 0 | 2115.0792 | 2097.7712 | -6021.8046 | 0 | -4935.0353 | 0 | 196.7669 | 183.272 | 77.99% | 80.98% | 81.02% | 100% | 100%
2021-07 | 100% | 193258.4165 | 182781.9321 | -10476.4844 | -5.421% | -11265.8737 | 988.7814 | -1028.6966 | 2011.0301 | 0 | 563.4072 | 1837.9053 | 0 | 0 | -3583.0381 | 0 | 170.3596 | 181.0362 | 81.28% | 83.98% | 80.87% | 100% | 100%
2021-08 | 100% | 182745.4465 | 141746.4849 | -40998.9616 | -22.44% | -37027.4023 | 3127.6598 | -897.2447 | 2113.1288 | 0 | 142.9195 | 575.4299 | -6277.5383 | 0 | -2755.9143 | 0 | 136.2709 | 170.7158 | 78.8% | 80.13% | 81.1% | 99.56% | 99.36%
2021-09 | 100% | 135984.2995 | 137015.023 | 1030.7235 | 0.758% | 3418.6311 | -1280.0199 | -887.3932 | 1246.9903 | 0 | 149.4656 | 1386.2173 | 0 | 0 | -3003.1679 | 0 | 125.4642 | 122.4195 | 82.73% | 83.57% | 84.15% | 100% | 100%
2021-10 | 100% | 103099.5586 | 110839.204 | 7739.6454 | 7.507% | 14637.9973 | 266.735 | -809.0667 | 538.8077 | 0 | 0 | -3149.4891 | 0 | -804.3519 | -2940.9869 | 0 | 104.2842 | 91.5043 | 80.52% | 79.3% | 85.36% | 97.93% | 96.24%
2021-11 | 100% | 39998.9607 | 39299.3216 | -699.6392 | -1.749% | 34.5134 | -9.3881 | -290.3389 | 245.5824 | -207.1765 | 0 | 401.351 | 0 | 0 | -874.1825 | 0 | 35.0668 | 35.011 | 84.9% | 80.71% | 86.55% | 100% | 100%
2021-12 | 100% | 43333.6974 | 21627.7618 | -21705.9356 | -50.09% | -7248.7382 | 1081.3641 | -286.5627 | 317.3597 | -13162.86 | 0 | 372.5228 | 0 | 0 | -2779.0213 | 0 | 32.1319 | 38.444 | 50.99% | 46.95% | 85.39% | 100% | 100%
2022-01 | 100% | 65982.2814 | 34919.5393 | -31062.7421 | -47.08% | -30616.4044 | -652.7238 | -282.4298 | 261.0514 | 532.6657 | 0 | 347.7851 | 0 | 0 | -652.6861 | 0 | 30.6001 | 56.1945 | 86.45% | 80.05% | 88.95% | 100% | 100%
2022-02 | 100% | 78950.2752 | 76462.6736 | -2487.6017 | -3.151% | -5403.36 | 745.6849 | -636.1721 | 964.0097 | 2301.0443 | 0 | 744.0043 | 0 | 0 | -1202.8129 | 0 | 65.6695 | 70.4871 | 88.21% | 84.02% | 84.85% | 100% | 100%
2022-03 | 99.87% | 108523.8933 | 169577.4003 | 61053.507 | 56.26% | 70214.3597 | -5345.2452 | -1550.1644 | -2653.262 | 1755.7944 | 244.6324 | 1735.7863 | 0 | 0 | -3348.3942 | 0 | 154.0418 | 93.9295 | 83.4% | 81.72% | 87.53% | 100% | 100%
2022-04 | 100% | 160467.8408 | 149331.5377 | -11136.3031 | -6.94% | -584.2819 | 2655.8831 | -1519.7975 | 2111.0723 | -1440.8242 | 374.1135 | -2876.2981 | -7072.4275 | 0 | -2783.7428 | 0 | 144.5144 | 145.1624 | 78.28% | 77.08% | 83.75% | 98.2% | 97.07%
2022-05 | 100% | 125981.4234 | 188113.0497 | 62131.6263 | 49.32% | 82348.4396 | -2751.0266 | -2003.1843 | 309.0444 | 0 | 240.7483 | -370.8715 | -4363.4013 | -7387.0401 | -3891.0822 | 0 | 188.5378 | 114.7012 | 75.59% | 76.59% | 83.21% | 98.9% | 98.73%
2022-06 | 100% | 195997.3563 | 199007.3145 | 3009.9582 | 1.536% | 10463.5019 | -1108.466 | -2089.4712 | 2529.3046 | 0 | 1902.9865 | 1453.5707 | -6001.7506 | 0 | -4139.7178 | 0 | 192.77 | 183.272 | 78.21% | 80.87% | 81.02% | 99.72% | 99.7%
2022-07 | 100% | 193258.4165 | 179408.6716 | -13849.7449 | -7.166% | -1517.3804 | 1254.8303 | -2042.3688 | 1810.9667 | 0 | 535.9815 | -7221.1608 | -2681.228 | -100.4894 | -3888.896 | 0 | 179.5148 | 181.0362 | 75.71% | 78.16% | 80.87% | 95.58% | 95.15%
2022-08 | 100% | 182745.4465 | 173312.4355 | -9433.011 | -5.162% | -4602.6485 | 341.2546 | -1963.5949 | 2436.2878 | 0 | 223.7192 | 1783.0349 | -3248.1809 | 0 | -4402.8833 | 0 | 166.3112 | 170.7158 | 78.95% | 81.83% | 81.1% | 100% | 100%
2022-09 | 100% | 135984.2995 | 131296.9552 | -4687.3443 | -3.447% | -1985.7566 | 382.5983 | -1531.5572 | 1411.8658 | 0 | 159.7316 | -609.7261 | 0 | 0 | -2514.5 | 0 | 120.5752 | 122.4195 | 82.49% | 82.35% | 84.15% | 98.93% | 98.54%
2022-10 | 100% | 103099.5586 | 95883.3527 | -7216.2059 | -6.999% | -5815.2173 | 255.2387 | -1152.2739 | 737.9591 | 0 | 0 | 973.6092 | 0 | 0 | -2215.5217 | 0 | 86.3496 | 91.5043 | 84.12% | 82.82% | 85.36% | 100% | 100%
2022-11 | 100% | 39998.9607 | 49751.324 | 9752.3633 | 24.38% | 10862.6966 | 66.1468 | -621.9312 | 305.7537 | 126.0269 | 0 | 508.1401 | 0 | 0 | -1494.4696 | 0 | 44.2157 | 35.011 | 85.24% | 80.9% | 86.55% | 100% | 100%
2022-12 | 100% | 43333.6974 | 19525.8537 | -23807.8437 | -54.94% | -12236.1564 | 889.1288 | -405.205 | 305.6759 | -11244.5482 | 0 | 319.0047 | 0 | 0 | -1435.7436 | 0 | 27.8252 | 38.444 | 53.16% | 49.03% | 85.39% | 100% | 100%
2023-01 | 100% | 65982.2814 | 29855.2295 | -36127.0519 | -54.75% | -34261.7943 | -981.4248 | -401.5037 | 306.411 | -32.2604 | 0 | 306.44 | 0 | 0 | -1062.9197 | 0 | 27.5587 | 56.1945 | 82.07% | 76.94% | 88.95% | 100% | 100%
2023-02 | 100% | 78950.2752 | 66568.828 | -12381.4473 | -15.68% | -10380.5725 | 1513.6491 | -945.7618 | 657.4644 | -2565.3179 | 0 | 698.3595 | 0 | 0 | -1359.2681 | 0 | 61.2795 | 70.4871 | 82.3% | 77.51% | 84.85% | 100% | 100%
2023-03 | 99.87% | 108523.8933 | 108670.7898 | 146.8965 | 0.1354% | 5276.9314 | -1389.684 | -1562.522 | 747.024 | -2120.7504 | 98.8959 | 1119.683 | 0 | 0 | -2022.6813 | 0 | 98.4055 | 93.9295 | 83.66% | 80.54% | 87.53% | 100% | 100%
2023-04 | 100% | 160467.8408 | 138842.4589 | -21625.3819 | -13.48% | -14798.6822 | 2090.474 | -2115.7946 | 1765.5606 | 0 | 344.2177 | -3155.4775 | -3095.8947 | 0 | -2659.7852 | 0 | 131.7633 | 145.1624 | 79.83% | 78.78% | 83.75% | 98.2% | 96.78%
2023-05 | 100% | 125981.4234 | 189545.8957 | 63564.4723 | 50.46% | 81222.5421 | -3227.7742 | -3001.0333 | 1877.0467 | 0 | 267.7421 | -2023.5514 | -6129.1363 | -904.2904 | -4517.0731 | 0 | 187.6109 | 114.7012 | 76.54% | 77.74% | 83.21% | 98.84% | 97.91%
2023-06 | 100% | 195997.3563 | 203679.85 | 7682.4937 | 3.92% | 13343.4898 | -699.3549 | -3152.2587 | 954.7777 | 0 | 1866.8717 | 2075.6488 | -1484.3955 | 0 | -5222.2851 | 0 | 195.4523 | 183.272 | 78.95% | 81.47% | 81.02% | 100% | 100%
2023-07 | 100% | 193258.4165 | 188561.8435 | -4696.573 | -2.43% | 356.0317 | 618.0545 | -3014.3855 | 1041.3524 | 0 | 573.2662 | 1902.6859 | -1873.7013 | 0 | -4299.8768 | 0 | 181.2284 | 181.0362 | 78.82% | 81.63% | 80.87% | 99.94% | 99.98%
2023-08 | 100% | 182745.4465 | 160360.4227 | -22385.0238 | -12.25% | -18220.1394 | 680.0633 | -2634.9867 | 1704.2441 | 0 | 207.0241 | 1638.9501 | -2083.9986 | 0 | -3676.1807 | 0 | 153.7295 | 170.7158 | 79.03% | 81.73% | 81.1% | 99.98% | 100%
2023-09 | 100% | 135984.2995 | 158333.52 | 22349.2204 | 16.44% | 31954.0482 | -4994.4228 | -2662.8201 | 407.3174 | 0 | 192.7139 | 1619.0011 | 0 | 0 | -4166.6172 | 0 | 150.9096 | 122.4195 | 79.48% | 81.96% | 84.15% | 100% | 100%
2023-10 | 100% | 103099.5586 | 79750.9788 | -23348.5798 | -22.65% | -22621.4 | 538.6415 | -1356.1047 | 332.3791 | 0 | 0 | 804.6535 | 0 | 0 | -1046.7492 | 0 | 71.6793 | 91.5043 | 84.29% | 82.66% | 85.36% | 100% | 100%
2023-11 | 100% | 39998.9607 | 52168.2337 | 12169.2729 | 30.42% | 13449.4152 | -87.1779 | -915.6946 | 650.617 | 39.3865 | 0 | 529.7526 | 0 | 0 | -1497.0259 | 0 | 46.4241 | 35.011 | 85.13% | 81.01% | 86.55% | 100% | 100%
2023-12 | 100% | 43333.6974 | 21581.3952 | -21752.3021 | -50.2% | -15149.6432 | 636.3877 | -507.4856 | 312.266 | -6295.5108 | 0 | 285.9895 | 0 | 0 | -1034.3057 | 0 | 25.3159 | 38.444 | 64.58% | 59.91% | 85.39% | 100% | 100%
2024-01 | 100% | 65982.2814 | 30245.7608 | -35736.5206 | -54.16% | -21277.522 | -931.5836 | -788.894 | -1322.1809 | -9436.7285 | 0 | 434.1847 | 0 | 0 | -2413.7963 | 0 | 38.3964 | 56.1945 | 59.68% | 55.36% | 88.95% | 100% | 100%
2024-02 | 100% | 78950.2752 | 48395.4449 | -30554.8303 | -38.7% | -31200.3575 | 213.1198 | -884.7961 | 317.4346 | 1312.7878 | 0 | 475.5378 | 0 | 0 | -788.5567 | 0 | 43.0904 | 70.4871 | 85.08% | 81.52% | 84.85% | 100% | 100%
2024-03 | 99.87% | 108523.8933 | 125481.7564 | 16957.8631 | 15.63% | 21890.5795 | -3671.8947 | -2387.334 | 626.5061 | 1270.5926 | 177.3089 | 1256.1136 | 0 | 0 | -2204.0088 | 0 | 112.634 | 93.9295 | 84.4% | 82.55% | 87.53% | 100% | 100%
2024-04 | 100% | 160467.8408 | 151300.6424 | -9167.1984 | -5.713% | 1570.0108 | 248.7557 | -3123.1796 | 1647.7197 | 0 | 957.7466 | -1814.2905 | -4954.1028 | -611.2618 | -3088.5966 | 0 | 146.4058 | 145.1624 | 78.29% | 78.23% | 83.75% | 98.22% | 97.79%
2024-05 | 100% | 125981.4234 | 208510.0845 | 82528.6611 | 65.51% | 106211.7691 | -7175.9192 | -4419.748 | 179.9358 | 0 | 1287.2419 | 617.0219 | -8366.2631 | 0 | -5805.3772 | 0 | 210.0566 | 114.7012 | 75.2% | 77.57% | 83.21% | 99.49% | 99.23%
2024-06 | 100% | 195997.3563 | 182427.7908 | -13569.5654 | -6.923% | -7955.9501 | 55.2167 | -3773.1226 | 2561.7376 | 0 | 1830.458 | 1440.4196 | -3653.8452 | 0 | -4074.4792 | 0 | 175.6464 | 183.272 | 78.68% | 80.9% | 81.02% | 99.45% | 99.77%
2024-07 | 100% | 193258.4165 | 192178.583 | -1079.8335 | -0.5588% | 7533.4312 | 97.5771 | -4111.1849 | 2502.4236 | 0 | 558.6498 | 1987.659 | -1742.7788 | -2909.1843 | -4996.4261 | 4.5475e-13 | 187.9257 | 181.0362 | 77.47% | 80.45% | 80.87% | 100% | 100%
2024-08 | 100% | 182745.4465 | 174784.1979 | -7961.2486 | -4.356% | -1769.65 | 131.8482 | -3781.9624 | 1999.1943 | 0 | 185.5645 | -114.7086 | 0 | 0 | -4611.5348 | 0 | 168.9506 | 170.7158 | 78.37% | 81.33% | 81.1% | 98.73% | 98.92%
2024-09 | 100% | 135984.2995 | 144466.175 | 8481.8755 | 6.237% | 16569.5895 | -3827.3279 | -3164.9774 | 1010.1657 | 0 | 175.0159 | 1470.319 | 0 | 0 | -3750.9092 | 0 | 137.2204 | 122.4195 | 79.76% | 81.85% | 84.15% | 100% | 100%
2024-10 | 100% | 103099.5586 | 91516.7992 | -11582.7594 | -11.23% | -9119.0503 | 348.6173 | -2046.9605 | 815.6155 | 0 | 0 | 932.1431 | 0 | 0 | -2513.1245 | 0 | 83.5408 | 91.5043 | 82.99% | 81.62% | 85.36% | 100% | 100%
2024-11 | 100% | 39998.9607 | 51189.5233 | 11190.5626 | 27.98% | 12753.2867 | 208.1176 | -1169.1636 | 1.3843 | 528.4277 | 0 | 523.1434 | 0 | 0 | -1654.6336 | 0 | 45.8241 | 35.011 | 84.63% | 80.1% | 86.55% | 100% | 100%
2024-12 | 100% | 43333.6974 | 30817.997 | -12515.7004 | -28.88% | -13218.3852 | 579.4921 | -691.0953 | 303.1306 | 937.323 | 0 | 303.0678 | 0 | 0 | -729.2332 | 0 | 26.97 | 38.444 | 86.57% | 80.55% | 85.39% | 100% | 100%

## Losses
Month | Soiling measured [kWh] | Soiling budget [kWh] | Snow measured [kWh] | Snow budget [kWh] | Clipping measured [kWh] | Clipping budget [kWh] | Availability measured [kWh] | Availability budget [kWh] | Curtailment measured [kWh] | Curtailment budget [kWh] | Data gaps measured [kWh] | Data gaps budget [kWh]
2021-01 | 725.1817 | 652.9971 | 17086.7378 | 1715.2057 | 0 | 0 | 175.5257 | 411.6494 | 0 | 0 | 0 | 0
2021-02 | 373.3246 | 1281.0986 | 25441.1375 | 2523.7642 | 0 | 0 | 0 | 816.0171 | 0 | 0 | 184.1478 | 0
2021-03 | 2687.4712 | 1949.4817 | 252.3603 | 1280.1597 | 0.22886 | 178.644 | 1033.0091 | 1265.5716 | 0 | 0 | 0 | 0
2021-04 | 1326.9498 | 2636.4834 | 0 | 0 | 751.0633 | 1037.6546 | 2798.9972 | 1720.9142 | 4985.2837 | 0 | 0 | 0
2021-05 | 566.8723 | 2971.7317 | 0 | 0 | 848.1153 | 1587.633 | 2529.5309 | 1935.5608 | 3868.404 | 0 | 491.1759 | 0
2021-06 | 1607.2207 | 3229.3798 | 0 | 0 | 170.4115 | 2285.4907 | 0 | 2097.7712 | 6021.8046 | 0 | 0 | 0
2021-07 | 796.3999 | 2807.43 | 0 | 0 | 0.62882 | 564.036 | 0 | 1837.9053 | 0 | 0 | 0 | 0
2021-08 | 165.5203 | 2278.6491 | 0 | 0 | 45.4844 | 188.4039 | 918.999 | 1494.4289 | 6277.5383 | 0 | 0 | 0
2021-09 | 866.5133 | 2113.5037 | 0 | 0 | 15.5394 | 165.005 | 0 | 1386.2173 | 0 | 0 | 0 | 0
2021-10 | 1263.9184 | 1802.7261 | 0 | 0 | 0 | 0 | 4333.2792 | 1183.7901 | 0 | 0 | 804.3519 | 0
2021-11 | 371.7856 | 617.3681 | 612.5815 | 405.405 | 0 | 0 | 0 | 401.351 | 0 | 0 | 0 | 0
2021-12 | 267.4791 | 584.8388 | 14314.9925 | 1152.1325 | 0 | 0 | 0 | 372.5228 | 0 | 0 | 0 | 0
2022-01 | 290.6382 | 551.6895 | 916.4388 | 1449.1045 | 0 | 0 | 0 | 347.7851 | 0 | 0 | 0 | 0
2022-02 | 204.0331 | 1168.0428 | 0 | 2301.0443 | 0 | 0 | 0 | 744.0043 | 0 | 0 | 0 | 0
2022-03 | 5327.0607 | 2673.7986 | 0 | 1755.7944 | 0.38548 | 245.0179 | 0 | 1735.7863 | 0 | 0 | 0 | 0
2022-04 | 380.7065 | 2491.7788 | 1440.8242 | 0 | 606.5889 | 980.7024 | 4502.7592 | 1626.4611 | 7072.4275 | 0 | 0 | 0
2022-05 | 2848.0925 | 3157.1369 | 0 | 0 | 1445.9364 | 1686.6848 | 2427.1912 | 2056.3197 | 4363.4013 | 0 | 7387.0401 | 0
2022-06 | 631.4005 | 3160.7051 | 0 | 0 | 333.9019 | 2236.8884 | 599.5901 | 2053.1608 | 6001.7506 | 0 | 0 | 0
2022-07 | 1135.3418 | 2946.3085 | 0 | 0 | 55.9563 | 591.9378 | 9149.984 | 1928.8232 | 2681.228 | 0 | 100.4894 | 0
2022-08 | 282.417 | 2718.7048 | 0 | 0 | 1.0695 | 224.7887 | 0 | 1783.0349 | 3248.1809 | 0 | 0 | 0
2022-09 | 634.092 | 2045.9578 | 0 | 0 | 0 | 159.7316 | 1951.6411 | 1341.915 | 0 | 0 | 0 | 0
2022-10 | 744.6945 | 1482.6535 | 0 | 0 | 0 | 0 | 0 | 973.6092 | 0 | 0 | 0 | 0
2022-11 | 475.88 | 781.6338 | 387.246 | 513.2729 | 0 | 0 | 0 | 508.1401 | 0 | 0 | 0 | 0
2022-12 | 195.1426 | 500.8185 | 12231.1606 | 986.6125 | 0 | 0 | 0 | 319.0047 | 0 | 0 | 0 | 0
2023-01 | 179.693 | 486.104 | 1309.0937 | 1276.8333 | 0 | 0 | 0 | 306.44 | 0 | 0 | 0 | 0
2023-02 | 438.9187 | 1096.3831 | 4725.1926 | 2159.8747 | 0 | 0 | 0 | 698.3595 | 0 | 0 | 0 | 0
2023-03 | 977.7314 | 1724.7555 | 3253.3399 | 1132.5894 | 59.1549 | 158.0508 | 0 | 1119.683 | 0 | 0 | 0 | 0
2023-04 | 488.2776 | 2253.8382 | 0 | 0 | 542.8371 | 887.0549 | 4626.6274 | 1471.1499 | 3095.8947 | 0 | 0 | 0
2023-05 | 1239.7607 | 3116.8073 | 0 | 0 | 1397.3968 | 1665.1389 | 4053.6035 | 2030.0521 | 6129.1363 | 0 | 904.2904 | 0
2023-06 | 2240.5462 | 3195.3239 | 0 | 0 | 394.517 | 2261.3887 | 0 | 2075.6488 | 1484.3955 | 0 | 0 | 0
2023-07 | 1909.0391 | 2950.3914 | 0 | 0 | 19.492 | 592.7581 | 28.8102 | 1931.4961 | 1873.7013 | 0 | 0 | 0
2023-08 | 799.6066 | 2503.8508 | 0 | 0 | 0 | 207.0241 | 3.175 | 1642.1251 | 2083.9986 | 0 | 0 | 0
2023-09 | 2061.1011 | 2468.4186 | 0 | 0 | 0 | 192.7139 | 0 | 1619.0011 | 0 | 0 | 0 | 0
2023-10 | 892.9815 | 1225.3606 | 0 | 0 | 0 | 0 | 0 | 804.6535 | 0 | 0 | 0 | 0
2023-11 | 164.2616 | 814.8786 | 495.7171 | 535.1036 | 0 | 0 | 0 | 529.7526 | 0 | 0 | 0 | 0
2023-12 | 136.7205 | 448.9865 | 7180.0142 | 884.5035 | 0 | 0 | 0 | 285.9895 | 0 | 0 | 0 | 0
2024-01 | 2010.9256 | 688.7447 | 11245.8313 | 1809.1028 | 0 | 0 | 0 | 434.1847 | 0 | 0 | 0 | 0
2024-02 | 429.1317 | 746.5662 | 157.9476 | 1470.7354 | 0 | 0 | 0 | 475.5378 | 0 | 0 | 0 | 0
2024-03 | 1308.4065 | 1934.9126 | 0 | 1270.5926 | 0 | 177.3089 | 0 | 1256.1136 | 0 | 0 | 0 | 0
2024-04 | 815.3341 | 2463.0538 | 0 | 0 | 11.6504 | 969.397 | 3422.0019 | 1607.7114 | 4954.1028 | 0 | 611.2618 | 0
2024-05 | 3241.1835 | 3421.1193 | 0 | 0 | 540.4742 | 1827.716 | 1611.236 | 2228.2578 | 8366.2631 | 0 | 0 | 0
2024-06 | 304.4627 | 2866.2002 | 0 | 0 | 198.0039 | 2028.4619 | 421.434 | 1861.8535 | 3653.8452 | 0 | 0 | 0
2024-07 | 533.7575 | 3036.1811 | 0 | 0 | 51.3442 | 609.994 | 0 | 1987.659 | 1742.7788 | 0 | 2909.1843 | 0
2024-08 | 731.9122 | 2731.1066 | 0 | 0 | 40.2496 | 225.8141 | 1905.8771 | 1791.1685 | 0 | 0 | 0 | 0
2024-09 | 1231.564 | 2241.7297 | 0 | 0 | 0 | 175.0159 | 0 | 1470.319 | 0 | 0 | 0 | 0
2024-10 | 603.8917 | 1419.5072 | 0 | 0 | 0 | 0 | 0 | 932.1431 | 0 | 0 | 0 | 0
2024-11 | 803.328 | 804.7123 | 0 | 528.4277 | 0 | 0 | 0 | 523.1434 | 0 | 0 | 0 | 0
2024-12 | 172.6678 | 475.7985 | 0 | 937.323 | 0 | 0 | 0 | 303.0678 | 0 | 0 | 0 | 0

## Contract
period | test | basis | measured | guaranteed | guaranteed_effective | pass | shortfall_kwh | damages | bonus | excluded_share | data_share
2021 | availability | time | 99.84% | 98% |  | PASS | 0 | 0 | 143.1386 | 1.385%
2022 | availability | time | 99.8% | 98% |  | PASS | 0 | 0 | 132.107 | 1.724%
2023 | availability | time | 99.98% | 98% |  | PASS | 0 | 0 | 199.7905 | 1.284%
2024 | availability | time | 99.85% | 98% |  | PASS | 0 | 0 | 149.7374 | 1.258%
2021 | performance_ratio | pr_wc | 80.25% | 78% | 76% | PASS | 0 | 0 | 0 |  | 97.74%
2022 | performance_ratio | pr_wc | 82.19% | 77.61% | 75.61% | PASS | 0 | 0 | 0 |  | 97.35%
2023 | performance_ratio | pr_wc | 81.61% | 77.22% | 75.22% | PASS | 0 | 0 | 0 |  | 97.87%
2024 | performance_ratio | pr_wc | 81.34% | 76.84% | 74.84% | PASS | 0 | 0 | 0 |  | 97.76%
Example clauses only (configs/contract_example.yaml); check against the actual contract.

## QC
check | status | message
clock | ok | labelling offset -0.7 min
clear_days | info | 220 clear days of 1450
orientation | ok | fitted tilt 26.5 deg (nominal 25), azimuth 178.1 deg (nominal 180)
level_clearsky | ok | level +5.3% against the clear-sky model on clear days (model uncertainty a few %)
shading | ok | no recurring low-sun shading of the sensor
sensor_soiling | ok | no decline-and-recovery pattern beyond 2.5%
drift | ok | no sustained level change beyond 2.5% against the baseline year (3 references: cs, ref, plant)
level_reference | ok | 2021: level +4.4% against poa_ref
level_reference | ok | 2022: level +3.9% against poa_ref
level_reference | ok | 2023: level +3.1% against poa_ref
gaps | info | 133 daylight intervals filled from the reference

## Downtime
inverter | start | end | hours | energy_kwh | category
INV01 | 2021-01-03 09:30 | 2021-01-03 15:15 | 5.75 | 178.0777 | outage
INV01 | 2021-04-12 08:00 | 2021-04-12 16:15 | 8.25 | 1127.4163 | planned_maintenance
INV01 | 2021-04-20 07:15 | 2021-04-20 10:15 | 3 | 370.6796 | unlogged
INV01 | 2021-10-08 09:45 | 2021-10-08 15:15 | 5.5 | 1107.2094 | grid_outage
INV01 | 2021-10-18 07:45 | 2021-10-18 08:30 | 0.75 | 13.5149 | outage
INV01 | 2022-04-17 08:00 | 2022-04-17 16:15 | 8.25 | 1465.4051 | planned_maintenance
INV01 | 2022-05-27 13:00 | 2022-05-27 19:15 | 6.25 | 562.8605 | outage
INV01 | 2022-05-28 06:00 | 2022-05-28 08:45 | 2.75 | 187.3934 | outage
INV01 | 2022-06-10 07:30 | 2022-06-10 12:00 | 4.5 | 611.6102 | outage
INV01 | 2022-07-14 15:00 | 2022-07-14 19:30 | 4.5 | 519.826 | force_majeure
INV01 | 2022-07-15 06:15 | 2022-07-15 19:30 | 13.25 | 1813.8868 | force_majeure
INV01 | 2022-09-04 06:45 | 2022-09-04 15:30 | 8.75 | 1433.7436 | outage
INV01 | 2023-04-14 08:00 | 2023-04-14 16:15 | 8.25 | 1328.5364 | planned_maintenance
INV01 | 2023-05-28 10:30 | 2023-05-28 13:00 | 2.5 | 616.6587 | grid_outage
INV01 | 2024-04-17 08:00 | 2024-04-17 16:15 | 8.25 | 1066.3147 | planned_maintenance
INV01 | 2024-06-21 05:45 | 2024-06-21 08:00 | 2.25 | 107.6482 | grid_outage
INV02 | 2021-04-27 08:00 | 2021-04-27 16:15 | 8.25 | 1343.2388 | planned_maintenance
INV02 | 2021-10-08 09:45 | 2021-10-08 15:15 | 5.5 | 1107.2094 | grid_outage
INV02 | 2022-04-28 08:00 | 2022-04-28 16:15 | 8.25 | 1511.5904 | planned_maintenance
INV02 | 2022-07-14 15:00 | 2022-07-14 19:30 | 4.5 | 519.826 | force_majeure
INV02 | 2022-07-15 06:15 | 2022-07-15 19:30 | 13.25 | 1813.8868 | force_majeure
INV02 | 2022-09-02 13:30 | 2022-09-02 18:30 | 5 | 554.5695 | outage
INV02 | 2023-04-21 08:00 | 2023-04-21 16:15 | 8.25 | 1756.0023 | planned_maintenance
INV02 | 2023-05-28 10:30 | 2023-05-28 13:00 | 2.5 | 616.6587 | grid_outage
INV02 | 2024-04-24 08:00 | 2024-04-24 16:15 | 8.25 | 720.4114 | planned_maintenance
INV02 | 2024-06-21 05:45 | 2024-06-21 08:00 | 2.25 | 107.6482 | grid_outage
INV03 | 2021-03-20 08:45 | 2021-03-20 15:15 | 6.5 | 1042.8319 | outage
INV03 | 2021-05-13 08:00 | 2021-05-13 11:00 | 3 | 575.1432 | planned_maintenance
INV03 | 2021-05-13 15:00 | 2021-05-13 16:15 | 1.25 | 223.1768 | planned_maintenance
INV03 | 2021-08-12 06:30 | 2021-08-12 10:30 | 4 | 442.3476 | outage
INV03 | 2021-08-15 12:15 | 2021-08-15 14:30 | 2.25 | 493.6287 | grid_command
INV03 | 2021-10-08 09:45 | 2021-10-08 15:15 | 5.5 | 1107.2094 | grid_outage
INV03 | 2022-04-27 08:00 | 2022-04-27 16:15 | 8.25 | 1602.5691 | planned_maintenance
INV03 | 2022-07-14 15:00 | 2022-07-14 19:30 | 4.5 | 519.826 | force_majeure
INV03 | 2022-07-15 06:15 | 2022-07-15 19:30 | 13.25 | 1813.8868 | force_majeure
INV03 | 2023-04-27 08:00 | 2023-04-27 16:15 | 8.25 | 1625.3075 | planned_maintenance
INV03 | 2023-05-28 10:30 | 2023-05-28 13:00 | 2.5 | 616.6587 | grid_outage
INV03 | 2024-04-30 08:00 | 2024-04-30 16:15 | 8.25 | 1700.7669 | planned_maintenance
INV03 | 2024-06-21 05:45 | 2024-06-21 08:00 | 2.25 | 107.6482 | grid_outage
INV04 | 2021-05-10 08:00 | 2021-05-10 16:15 | 8.25 | 1770.5522 | planned_maintenance
INV04 | 2021-10-08 09:45 | 2021-10-08 15:15 | 5.5 | 1107.2094 | grid_outage
INV04 | 2022-05-16 08:00 | 2022-05-16 16:15 | 8.25 | 1723.0148 | planned_maintenance
INV04 | 2022-07-14 15:00 | 2022-07-14 19:30 | 4.5 | 519.826 | force_majeure
INV04 | 2022-07-15 06:15 | 2022-07-15 19:30 | 13.25 | 1813.8868 | force_majeure
INV04 | 2023-05-04 08:00 | 2023-05-04 16:15 | 8.25 | 1677.6427 | planned_maintenance
INV04 | 2023-05-28 10:30 | 2023-05-28 13:00 | 2.5 | 616.6587 | grid_outage
INV04 | 2023-07-06 18:30 | 2023-07-06 19:30 | 1 | 29.4537 | unlogged
INV04 | 2023-08-17 19:00 | 2023-08-17 19:15 | 0.25 | 3.2463 | outage
INV04 | 2024-05-03 08:00 | 2024-05-03 16:15 | 8.25 | 1653.5903 | planned_maintenance
INV04 | 2024-06-21 05:45 | 2024-06-21 08:00 | 2.25 | 107.6482 | grid_outage
INV04 | 2024-08-04 12:00 | 2024-08-04 18:30 | 6.5 | 720.556 | outage
INV04 | 2024-08-08 06:30 | 2024-08-08 19:15 | 12.75 | 1234.7928 | outage